## Nomenclature
FIG. 10-1
Nomenclature
A | = | area of heat transfer surface, sq ft | NR | = | modified Reynolds number, (in • lb)/(sq ft • s • cp)
Ai | = | inside surface of tube, sq ft | Nt | = | number of tubes
Ab | = | outside bare tube surface, sq ft | ΔP | = | pressure drop, psi
Ax | = | outside extended surface of tube, sq ft | PF | = | fan total pressure, inches of water
At | = | tube inside cross-sectional area, sq in. (see Fig 9-25) | ρa | = | density of air, lb/cu ft
ACFM | = | actual cubic feet per minute | ρw | = | density of water, lb./cu ft
APF | = | total external area/ft of fintube, sq ft/ft | P | = | temperature ratio (see Fig 10-8)
APSF | = | external area of fintube, sq ft/sq ft of bundle face area | PWL | = | sound pressure level
AR | = | area ratio of fintube compared to the exterior area of 1 in. OD bare tube | PWLN | = | PWL for Nf fans
B | = | correction factor, psi (see Fig 10-14) | Q | = | heat transferred, Btu/h
Cp | = | specific heat at average temperature, Btu/(lb • °F) | rd | = | fouling resistance (fouling factor), (hr • ft2 • °F/Btu)
CMTD | = | corrected mean temperature difference, °F | rf | = | fluid film resistance (reciprocal of film coefficient)
dB(A) | = | overall weighted level of sound at a point distant from noise source based on "A" weighting system | rmb | = | metal resistance referred to outside bare surface
D | = | fan diameter, ft | rmx | = | metal resistance referred to outside extended surface
Di | = | inside tube diameter, in. | R | = | distance in feet (see Eq 10-6)
Do | = | outside, tube diameter, in. | R | = | temperature ratio (see Fig 10-8)
DR | = | density ratio, the ratio of actual air density to the density of dry air at 70 °F and 14.7 psia, 0.0749 lb/cu ft (see Fig 10-16) | RPM | = | fan speed, rotations per minute
f | = | friction factor (see Fig 10-15) | S | = | specific gravity (water = 1.0)
F | = | correction factor (see Fig 10-8) | SPL | = | sound pressure level
Fa | = | total face area of bundles, sq ft | t | = | temperature air side, °F
Fp | = | air pressure drop factor, in. of water per row of tubes | T | = | temperature tube side, °F
FAPF | = | fan area per fan, ft2/fan | U | = | overall heat transfer coefficient, Btu/(h • ft2 • °F)
FPM | = | fan tip speed, feet per minute | W | = | mass flow, lb/hr
g | = | local acceleration due to gravity, ft/s2 | Y | = | correction factor, psi/ft (see Fig 10-14)
G | = | mass velocity, lb/(sq ft • s) | Δt | = | temperature change, °F
Ga | = | air face mass velocity, lb/(hr • sq ft) of face area | μ | = | viscosity, cp
Gt | = | tubeside mass velocity, lb/(sq ft • s) | μw | = | viscosity at average tube wall temperature, cp
ha | = | air side film coefficient, Btu/(h • sq ft • °F) | φ | = | viscosity gradient correction
hs | = | shell side film coefficient based on outside tube area, Btu/(h • sq ft • °F)
ht | = | tube side film coefficient based on inside tube area, Btu/(h • sq ft • °F) | Subscripts
HP | = | fan horsepower | a | = | air side
J | = | J factor (see Fig 10-13) | b | = | bare tube surface basis
k | = | thermal conductivity, Btu/[(hr • sq ft • °F)/ft] | s | = | shell side
L | = | length of tube, ft | t | = | tube side
LMTD | = | log mean temperature difference, °F | x | = | extended tube surface basis
N | = | number of rows of tubes in direction of flow | 1 | = | inlet
Nf | = | number of fans | 2 | = | outlet
NP | = | number of tube passes

## Example 10-1
Example 10-1 Procedure for determining a rough, preliminary heat transfer surface area, required plot space, and fan power for an air-cooled exchanger |  |  |  | Example 10-1 Procedure for determining a rough, preliminary heat transfer surface area, required plot space, and fan power for an air-cooled exchanger
Required data |  |  |  | Required data
Fluid | = | Process Cooling Water |  | Fluid | = | Process Cooling Water
Heat Load, Q | = | 20000000 | Btu/hr | Heat Load, Q | = | 20000000 | Btu/hr
Temperature In | = | 300 | °F | Temperature In | = | 300 | °F
Temperature out | = | 150 | °F | Temperature out | = | 150 | °F
Ambient temperature | = | 100 | °F | Ambient temperature | = | 100 | °F
Fouling factor | = | 0.002 | hr-ft2-degF/Btu | Fouling factor | = | 0.002 | hr-ft2-degF/Btu
Heat release curve | = | Linear |  | Heat release curve | = | Linear
Cp air | = | 0.25 | Btu/lb-degF | Cp air | = | 0.25 | Btu/lb-degF
Basic Assumptions |  |  |  | Basic Assumptions
Type | = | Forced draft, 2 fans |  | Type | = | Forced draft, 2 fans
Fintube | = | 1 in OD, 5/8 in high fins |  | Fintube | = | 1 in OD, 5/8 in high fins
Tube pitch | = | 2-3/8 in triangular |  | Tube pitch | = | 2-3/8 in triangular
Bundle layout | = | 4 tube passes, 6 rows of tubes |  | Bundle layout | = | 4 tube passes, 6 rows of tubes
First Trial |  |  |  | First Trial
1. Pick an appropriate overall heat transfer coefficient, Ux | = | 5.2 | Btu/hr-ft2-degF (see Fig 10-10, for Process Water and 5/8 inch by 10) | 1. Pick an appropriate overall heat transfer coefficient, Ux | = | 5.2 | Btu/hr-ft2-degF (see Fig 10-10, for Process Water and 5/8 inch by 10)
2. Determine the appropriate external area of fintube per sq.sf. of bundle area | = | 169.6 | ft2/ft2 | 2. Determine the appropriate external area of fintube per sq.sf. of bundle area | = | 169.6 | ft2/ft2
3. Determine the LMTD correction factor | = | 1 | Dimensionless. Use 1.0 for 3 or more tube passes, otherwise use Figs. 10-8 or 10-9. | 3. Determine the LMTD correction factor | = | 1 | Dimensionless. Use 1.0 for 3 or more tube passes, otherwise use Figs. 10-8 or 10-9.
4. Assume t2 and calculate the CMTD, with countercurrent temperature profile. | = | 200 | degF | 4. Assume t2 and calculate the CMTD, with countercurrent temperature profile. | = | 200 | degF
Calculate CMTD = (F)(LMTD) | = | 72.1348 | degF | Calculate CMTD = (F)(LMTD) | = | 72.1348 | degF
5. Calculate Ax | = | 53319.0139 | sq. ft. | 5. Calculate Ax | = | 53319.0139 | sq. ft.
6. Based on APSF, calculate the air-side face area, Aa | = | 314.381 | sq. ft. | 6. Based on APSF, calculate the air-side face area, Aa | = | 314.381 | sq. ft.
7. Calculate the air side mass flow rate(Wa) using Aa and based on a typical face velocity of 600 Std. ft/min | = | 848828.6409 | lb/hr | 7. Calculate the air side mass flow rate(Wa) using Aa and based on a typical face velocity of 600 Std. ft/min | = | 848828.6409 | lb/hr
8. Check actual t2 from exchanger (t2,actual) | = | 194.2475 | °F | 8. Check actual t2 from exchanger (t2,actual) | = | 194.2475 | °F
9. Repeat steps 4 through 8 by iterating t2 until convergence is achieved | = | 196.2 | °F | 9. Repeat steps 4 through 8 by iterating t2 until convergence is achieved | = | 196.2 | °F
Recalculation of Step 4, CMTD | = | 73.6539 | °F | Recalculation of Step 4, CMTD | = | 73.6539 | °F
Recalculation of Step 5, Ax | = | 52219.2569 | sq. ft. | Recalculation of Step 5, Ax | = | 52219.2569 | sq. ft.
Recalculation of Step 6, Aa | = | 307.8966 | sq. ft. | Recalculation of Step 6, Aa | = | 307.8966 | sq. ft.
Recalculation of Step 7, Wa | = | 831320.7169 | sq. ft. | Recalculation of Step 7, Wa | = | 831320.7169 | sq. ft.
Recalculation of Step 8, t2,actual | = | 196.2324 | °F | Recalculation of Step 8, t2,actual | = | 196.2324 | °F
The recalculated Step 6, face area (Aa), shows a bay size of 10 ft X 30 ft (300 sq.ft) will be adequate. |  |  |  | The recalculated Step 6, face area (Aa), shows a bay size of 10 ft X 30 ft (300 sq.ft) will be adequate.
Bay width | = | 10 | ft | Bay width | = | 10 | ft
Bay length | = | 30 | ft | Bay length | = | 30 | ft
Calculate fan horsepower by extrapolating from two 40 BHP fans on a 15 ft X 45 ft unit. | = | 17.7778 | bhp per fan (two required) | Calculate fan horsepower by extrapolating from two 40 BHP fans on a 15 ft X 45 ft unit. | = | 17.7778 | bhp per fan (two required)
Length to width ratio is typically 3:1 |  |  |  | Length to width ratio is typically 3:1
Truck shippable units do not exceed 15 ft X 45 ft |  |  |  | Truck shippable units do not exceed 15 ft X 45 ft
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 10-2 Part 1
Example 10-2 Part 1 -- Procedure for estimating transfer surface, plot area, and horsepower | [6 empty] | Example 10-2 Part 1 -- Procedure for estimating transfer surface, plot area, and horsepower
Given Data: | [6 empty] | Given Data:
Required Data For Hot Fluid | [6 empty] | Required Data For Hot Fluid
Name and Phase | = | 48°API | hydrocarbon liquid |  |  |  | Name and Phase | = | 48°API | hydrocarbon liquid
Physical Props at avg temp | = | 200 | °F |  |  |  | Physical Props at avg temp | = | 200 | °F
Specific Heat Cp | = | 0.55 | Btu/(lb • °F) |  |  |  | Specific Heat Cp | = | 0.55 | Btu/(lb • °F)
Viscosity μ | = | 0.51 | cp |  |  |  | Viscosity μ | = | 0.51 | cp
Thermal Conductivity k | = | 0.0766 | Btu/[(hr • sq ft • °F)/ft] |  |  |  | Thermal Conductivity k | = | 0.0766 | Btu/[(hr • sq ft • °F)/ft]
Heat Load Q | = | 15000000 | Btu/hr |  |  |  | Heat Load Q | = | 15000000 | Btu/hr
Flow Quantity Wt | = | 273000 | lb/hr |  |  |  | Flow Quantity Wt | = | 273000 | lb/hr
Temperature In T1 | = | 250 | °F |  |  |  | Temperature In T1 | = | 250 | °F
Temperature Out T2 | = | 150 | °F |  |  |  | Temperature Out T2 | = | 150 | °F
Fouling Factor rdt | = | 0.001 | (hr • sq ft • °F)/Btu |  |  |  | Fouling Factor rdt | = | 0.001 | (hr • sq ft • °F)/Btu
Allowable Press Drop ΔPt | = | 5 | psi |  |  |  | Allowable Press Drop ΔPt | = | 5 | psi
Required Data For Air | [6 empty] | Required Data For Air
Ambient Temperature t1 | = | 100 | °F |  |  |  | Ambient Temperature t1 | = | 100 | °F
Elevation | = | Sea level | See Fig 10-16 for Altitude Correction |  |  |  | Elevation | = | Sea level | See Fig 10-16 for Altitude Correction
CPair | = | 0.24 | Btu/(lb • °F) |  |  |  | CPair | = | 0.24 | Btu/(lb • °F)
Air density, 70 degF, sea level | = | 0.0749 | lb/cu.ft |  |  |  | Air density, 70 degF, sea level | = | 0.0749 | lb/cu.ft
Density Ratio Air DR, air | = | 0.94 | dimensionless |  |  |  | Density Ratio Air DR, air | = | 0.94 | dimensionless
Basic Assumptions | [6 empty] | Basic Assumptions
Type | = | 2 | Fans, Forced Draft |  |  |  | Type | = | 2 | Fans, Forced Draft
Fintube Do | = | 1 | in. OD |  |  |  | Fintube Do | = | 1 | in. OD
|  | 0.625 | in. high fins | [5 empty] | 0.625 | in. high fins
Tube pitch | = | 2.5 | in. triangular (Δ) |  |  |  | Tube pitch | = | 2.5 | in. triangular (Δ)
Bundle Layout NP | = | 3 | tube passes |  |  |  | Bundle Layout NP | = | 3 | tube passes
N | = | 4 | rows of tubes |  |  |  | N | = | 4 | rows of tubes
L | = | 30 | ft long tubes |  |  |  | L | = | 30 | ft long tubes
Data Collected From Figures in Text | [6 empty] | Data Collected From Figures in Text
APSF | = | 107.2 | sq.ft./sq.ft. |  |  | Fig 10-11 | APSF | = | 107.2 | sq.ft./sq.ft. |  |  | Fig 10-11
APF | = | 5.58 | sq ft/ft |  |  | Fig 10-11 | APF | = | 5.58 | sq ft/ft |  |  | Fig 10-11
At | = | 0.5945 | in2 |  |  | Fig 9-25 | At | = | 0.5945 | in2 |  |  | Fig 9-25
Di | = | 0.87 | in. |  |  | Fig 9-25 | Di | = | 0.87 | in. |  |  | Fig 9-25
φ | = | 0.96 | dimensionless |  |  | Fig 10-19 | φ | = | 0.96 | dimensionless |  |  | Fig 10-19
k • [(Cp • μ)/k]1/3 | = | 0.12 | sq.ft./sq.ft. |  |  | Fig 10-12 | k • [(Cp • μ)/k]1/3 | = | 0.12 | sq.ft./sq.ft. |  |  | Fig 10-12
AR | = | 21.4 | sq ft/sq ft |  |  | Fig 10-11 | AR | = | 21.4 | sq ft/sq ft |  |  | Fig 10-11
To determine Approximate Air Temperature Rise | [6 empty] | To determine Approximate Air Temperature Rise
Δta | = | [(Ux+1)/10] • [((T1+T2)/2)-t1] |  |  |  |  | Δta | = | [(Ux+1)/10] • [((T1+T2)/2)-t1]
|  | See Intermediate Calculations below. | [6 empty] | See Intermediate Calculations below.
To determine t2 | [6 empty] | To determine t2
t2 | = | t1 + Δta |  |  |  |  | t2 | = | t1 + Δta
To determine LMTD | [6 empty] | To determine LMTD
LMTD | = | (GTTD-LTTD)/ln(GTTD/LTTD) |  |  |  | Fig 9-3 | LMTD | = | (GTTD-LTTD)/ln(GTTD/LTTD) |  |  |  | Fig 9-3
To determine CMTD | [6 empty] | To determine CMTD
CMTD | = | LMTD • F1 |  |  |  |  | CMTD | = | LMTD • F1
To determine Outside Extended Surface of Tube | [6 empty] | To determine Outside Extended Surface of Tube
Ax | = | Q/(Ux • CMTD) |  |  |  |  | Ax | = | Q/(Ux • CMTD)
To determine Total Face Area of Bundles | [6 empty] | To determine Total Face Area of Bundles
Fa | = | Ax/APSF |  |  |  |  | Fa | = | Ax/APSF
To determine the Unit Width | [6 empty] | To determine the Unit Width
Width | = | Fa/L |  |  |  |  | Width | = | Fa/L
To determine the Number of Tubes | [6 empty] | To determine the Number of Tubes
Nt | = | Ax/(APF • L) |  |  |  |  | Nt | = | Ax/(APF • L)
To determine the Tubeside Mass Velocity | [6 empty] | To determine the Tubeside Mass Velocity
Gt | = | (144 • Wt • Np)/(3600 • Nt • At) |  |  |  |  | Gt | = | (144 • Wt • Np)/(3600 • Nt • At)
To determine the Modified Reynolds Number | [6 empty] | To determine the Modified Reynolds Number
NR | = | (Di • Gt)/μ |  |  |  |  | NR | = | (Di • Gt)/μ
To determine the Tube-Side Pressure Drop | [6 empty] | To determine the Tube-Side Pressure Drop
ΔPt | = | [(f • Y • L • Np)/φ] + (B • Np) |  |  |  | Fig 10-14, 10-15 | ΔPt | = | [(f • Y • L • Np)/φ] + (B • Np) |  |  |  | Fig 10-14, 10-15
Intermediate Calculations (not shown) | [6 empty] | Intermediate Calculations (not shown)
1. Pick Approximate Overall Transfer Coefficient from Fig 10-10 | [6 empty] | 1. Pick Approximate Overall Transfer Coefficient from Fig 10-10
Ux |  |  |  | = | 4.2 | Btu/(h • ft2 • °F) | Ux |  |  |  | = | 4.2 | Btu/(h • ft2 • °F)
2. Calculate Approximate Air Temperature Rise | [6 empty] | 2. Calculate Approximate Air Temperature Rise
Δta | = | [(4.2+1)/10] • [((250+150)/2)-100] |  | = | 52 | °F | Δta | = | [(4.2+1)/10] • [((250+150)/2)-100] |  | = | 52 | °F
t2 | = | 100 + 52 |  | = | 152 | °F | t2 | = | 100 + 52 |  | = | 152 | °F
3. Calculate CMTD |  | hot side | cold side |  |  |  | 3. Calculate CMTD |  | hot side | cold side
Hydrocarbon |  | 250 | 150 |  |  |  | Hydrocarbon |  | 250 | 150
Air |  | 152 | 100 |  |  |  | Air |  | 152 | 100
|  | 98 | 50 | [5 empty] | 98 | 50
GTTD |  |  |  | = | 98 | °F | GTTD |  |  |  | = | 98 | °F
LTTD |  |  |  | = | 50 | °F | LTTD |  |  |  | = | 50 | °F
LMTD | = | (98-50)/[ln(98/50)] |  | = | 71.3283 | °F | LMTD | = | (98-50)/[ln(98/50)] |  | = | 71.3283 | °F
|  | Alternatively, use Fig. 9-3 LMTD diagram | [6 empty] | Alternatively, use Fig. 9-3 LMTD diagram
Use Fig 9-4 to Find F1 | [6 empty] | Use Fig 9-4 to Find F1
F1 |  |  |  | = | 1 |  | F1 |  |  |  | = | 1
CMTD | = | 71.3 • 1.0 |  | = | 71.3283 | °F | CMTD | = | 71.3 • 1.0 |  | = | 71.3283 | °F
4. Calculate Required Surface | [6 empty] | 4. Calculate Required Surface
Ax | = | 15000000/(4.2 • 53.5) |  | = | 50070.2733 | ft2 | Ax | = | 15000000/(4.2 • 53.5) |  | = | 50070.2733 | ft2
5. Calculate Face Area Using APSF factor from Fig 10-11 | [6 empty] | 5. Calculate Face Area Using APSF factor from Fig 10-11
Fa | = | 50,700/107.2 |  | = | 465 | ft2 | Fa | = | 50,700/107.2 |  | = | 465 | ft2
6. Calculate Unit Width with Assumed Tube Length | [6 empty] | 6. Calculate Unit Width with Assumed Tube Length
Width | = | 465/30 |  | = | 15.5 | ft | Width | = | 465/30 |  | = | 15.5 | ft
7. Calculate the Number of Tubes Using APF factor from Fig 10-11 | [6 empty] | 7. Calculate the Number of Tubes Using APF factor from Fig 10-11
Nt | = | 50,070/(5.58 • 30) |  | = | 299.1056 |  | Nt | = | 50,070/(5.58 • 30) |  | = | 299.1056
8. Calculate Tube-Side Mass Velocity from Assumed number of passes and reading At from Fig 9-25 for a 1 in. OD x 16 BWG tube | [6 empty] | 8. Calculate Tube-Side Mass Velocity from Assumed number of passes and reading At from Fig 9-25 for a 1 in. OD x 16 BWG tube
Gt | = | (144 • 273000 • 3)/(3600 • 299 • 0.5945) |  | = | 184.233 | lb/(ft2 • sec) | Gt | = | (144 • 273000 • 3)/(3600 • 299 • 0.5945) |  | = | 184.233 | lb/(ft2 • sec)
9. Calculate Modified Reynolds number | [6 empty] | 9. Calculate Modified Reynolds number
NR | = | (0.87 • 184)/0.51 |  | = | 314.2799 |  | NR | = | (0.87 • 184)/0.51 |  | = | 314.2799
10. Calculate Tube-Side Pressure Drop using Equation from Fig 10-14 and Fig 10-15 | [6 empty] | 10. Calculate Tube-Side Pressure Drop using Equation from Fig 10-14 and Fig 10-15
Use Fig 10-14 to find Y and B | [6 empty] | Use Fig 10-14 to find Y and B
Y |  |  |  | = | 14.5 | psi/ft | Y |  |  |  | = | 14.5 | psi/ft
B |  |  |  | = | 0.25 | psi/tube pass | B |  |  |  | = | 0.25 | psi/tube pass
Use Fig 10-15 to find f using NR | [6 empty] | Use Fig 10-15 to find f using NR
f |  |  |  | = | 0.0024 |  | f |  |  |  | = | 0.0024
ΔPt | = | [(0.0024 • 14.5 • 30 • 3)/0.96] + (0.25 • 3) |  | = | 4.0125 | psi | ΔPt | = | [(0.0024 • 14.5 • 30 • 3)/0.96] + (0.25 • 3) |  | = | 4.0125 | psi
CONTINUED ON NEXT TAB "EXAMPLE 10-2 PART 2"
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 10-2 Part 2
Example 10-2 Part 2 -- Procedure for estimating transfer surface, plot area, and horsepower Continued | [6 empty] | Example 10-2 Part 2 -- Procedure for estimating transfer surface, plot area, and horsepower Continued
Given Data: | [6 empty] | Given Data:
Required Data For Hot Fluid | [6 empty] | Required Data For Hot Fluid
Name and Phase | = | 48 degAPI | hydrocarbon liquid |  |  |  | Name and Phase | = | 48 degAPI | hydrocarbon liquid
Physical Props at avg temp | = | 200 | °F |  |  |  | Physical Props at avg temp | = | 200 | °F
Specific Heat Cp | = | 0.55 | Btu/(lb • °F) |  |  |  | Specific Heat Cp | = | 0.55 | Btu/(lb • °F)
Viscosity μ | = | 0.51 | cp |  |  |  | Viscosity μ | = | 0.51 | cp
Thermal Conductivity k | = | 0.0766 | Btu/[(hr • sq ft • °F)/ft] |  |  |  | Thermal Conductivity k | = | 0.0766 | Btu/[(hr • sq ft • °F)/ft]
Heat Load Q | = | 15000000 | Btu/hr |  |  |  | Heat Load Q | = | 15000000 | Btu/hr
Flow Quantity Wt | = | 273000 | lb/hr |  |  |  | Flow Quantity Wt | = | 273000 | lb/hr
Temperature In T1 | = | 250 | °F |  |  |  | Temperature In T1 | = | 250 | °F
Temperature Out T2 | = | 150 | °F |  |  |  | Temperature Out T2 | = | 150 | °F
Fouling Factor rdt | = | 0.001 | (hr • sq ft • °F)/Btu |  |  |  | Fouling Factor rdt | = | 0.001 | (hr • sq ft • °F)/Btu
Allowable Press Drop ΔPt | = | 5 | psi |  |  |  | Allowable Press Drop ΔPt | = | 5 | psi
Required Data For Air | [6 empty] | Required Data For Air
Ambient Temperature t1 | = | 100 | °F |  |  |  | Ambient Temperature t1 | = | 100 | °F
Elevation | = | Sea Level | See Fig 10-16 for Altitude Correction |  |  |  | Elevation | = | Sea Level | See Fig 10-16 for Altitude Correction
CPair | = | 0.24 | Btu/(lb • °F) |  |  |  | CPair | = | 0.24 | Btu/(lb • °F)
Air density, seal level, 70 degF | = | 0.0749 | lb/cu ft |  |  |  | Air density, seal level, 70 degF | = | 0.0749 | lb/cu ft
Density Ratio Air DR, air | = | 0.94 | lb/cu ft |  |  |  | Density Ratio Air DR, air | = | 0.94 | dimensionless
Basic Assumptions | [6 empty] | Basic Assumptions
Type | = | 2 | Fans, Forced Draft |  |  |  | Type | = | 2 | Fans, Forced Draft
Fintube Do | = | 1 | in. OD |  |  |  | Fintube Do | = | 1 | in. OD
|  | 0.625 | in. high fins | [5 empty] | 0.625 | in. high fins
Tube pitch | = | 2.5 | in. triangular (Δ) |  |  |  | Tube pitch | = | 2.5 | in. triangular (Δ)
Bundle Layout NP | = | 3 | tube passes |  |  |  | Bundle Layout NP | = | 3 | tube passes
N | = | 4 | rows of tubes |  |  |  | N | = | 4 | rows of tubes
L | = | 30 | ft long tubes |  |  |  | L | = | 30 | ft long tubes
Data Collected From Figures in Text | [6 empty] | Data Collected From Figures in Text
APSF | = | 107.2 |  |  |  | Fig 10-11 | APSF | = | 107.2 |  |  |  | Fig 10-11
APF | = | 5.58 | sq ft/ft |  |  | Fig 10-11 | APF | = | 5.58 | sq ft/ft |  |  | Fig 10-11
At | = | 0.5945 | in2 |  |  | Fig 9-25 | At | = | 0.5945 | in2 |  |  | Fig 9-25
Di | = | 0.87 | in. |  |  | Fig 9-25 | Di | = | 0.87 | in. |  |  | Fig 9-25
φ | = | 0.96 |  |  |  | Fig 10-19 | φ | = | 0.96 |  |  |  | Fig 10-19
k • [(Cp • μ)/k]1/3 | = | 0.12 |  |  |  | Fig 10-12 | k • [(Cp • μ)/k]1/3 | = | 0.12 |  |  |  | Fig 10-12
AR | = | 21.4 | sq ft/sq ft |  |  | Fig 10-11 | AR | = | 21.4 | sq ft/sq ft |  |  | Fig 10-11
Calculated Data from Example 10-2 Part 1 | [6 empty] | Calculated Data from Example 10-2 Part 1
Assumed Ux | = | 4.2 | Btu/(h • ft2 • °F) |  |  |  | Assumed Ux | = | 4.2 | Btu/(h • ft2 • °F)
Δta | = | 52 | °F |  |  |  | Δta | = | 52 | °F
t2 | = | 152 | °F |  |  |  | t2 | = | 152 | °F
CMTD | = | 71.3283 | °F |  |  |  | CMTD | = | 71.3283 | °F
Ax | = | 50070.2733 | ft2 |  |  |  | Ax | = | 50070.2733 | ft2
Fa | = | 465 | ft2 |  |  |  | Fa | = | 465 | ft2
Width | = | 15.5 | ft |  |  |  | Width | = | 15.5 | ft
Nt | = | 299.1056 |  |  |  |  | Nt | = | 299.1056
Gt | = | 184.233 | lb/(ft2 • sec) |  |  |  | Gt | = | 184.233 | lb/(ft2 • sec)
NR | = | 314.2799 |  |  |  |  | NR | = | 314.2799
ΔPt | = | 4.0125 | psi |  |  |  | ΔPt | = | 4.0125 | psi
To determine the Tube-Side Film Coefficient | [6 empty] | To determine the Tube-Side Film Coefficient
ht | = | [J • (k • ((Cp • μ)/k)1/3) • φ]/Di |  |  |  | Fig 10-13 | ht | = | [J • (k • ((Cp • μ)/k)1/3) • φ]/Di |  |  |  | Fig 10-13
|  | See Intermediate Calculations below. | [6 empty] | See Intermediate Calculations below.
To determine Air Quality | [6 empty] | To determine Air Quality
Wa | = | Q/(0.24 • Δta) |  |  |  |  | Wa | = | Q/(0.24 • Δta)
To determine Air Face Mass Velocity | [6 empty] | To determine Air Face Mass Velocity
Ga | = | Wa/Fa |  |  |  |  | Ga | = | Wa/Fa
To determine Ax/Ai | [6 empty] | To determine Ax/Ai
Ax/Ai | = | (AR • Do)/Di |  |  |  |  | Ax/Ai | = | (AR • Do)/Di
To determine Overall Transfer Coefficient | [6 empty] | To determine Overall Transfer Coefficient
1/Ux | = | [(1/ht) • (Ax/Ai)] + [(rdt • (Ax/Ai)] + rmx + (1/ha) |  |  |  |  | 1/Ux | = | [(1/ht) • (Ax/Ai)] + [(rdt • (Ax/Ai)] + rmx + (1/ha)
To determine Minimum Fan Area Per Fan | [6 empty] | To determine Minimum Fan Area Per Fan
FAPF | = | (0.4 • Fa)/Nf |  |  |  |  | FAPF | = | (0.4 • Fa)/Nf
To determine Fan Diameter | [6 empty] | To determine Fan Diameter
D | = | [(4 • FAPF)/π]0.5 |  |  |  |  | D | = | [(4 • FAPF)/π]0.5
To determine Air Static Pressure Drop | [6 empty] | To determine Air Static Pressure Drop
ΔPa | = | (Fp • N)/DR |  |  |  |  | ΔPa | = | (Fp • N)/DR
To determine Actual Air Volume | [6 empty] | To determine Actual Air Volume
ACFM | = | Wa/(DR • 60 • DR, air) |  |  |  |  | ACFM | = | Wa/(DR • 60 • DR, air)
To determine the fan Total Pressure | [6 empty] | To determine the fan Total Pressure
PF | = | ΔPa + [ACFM/(4005 • ((π • D2)/4))]2 • DR |  |  |  |  | PF | = | ΔPa + [ACFM/(4005 • ((π • D2)/4))]2 • DR
To determine the Brake Horsepower Per Fan | [6 empty] | To determine the Brake Horsepower Per Fan
bhp | = | [(ACFM/fan) • PF]/(6356 • 0.7) |  |  |  |  | bhp | = | [(ACFM/fan) • PF]/(6356 • 0.7)
Intermediate Calculations (not shown) | [6 empty] | Intermediate Calculations (not shown)
11. Calculate Tube-Side Film Coefficient using Equation from Fig 10-13 | [6 empty] | 11. Calculate Tube-Side Film Coefficient using Equation from Fig 10-13
Using Fig 10-13 to find J Factor using NR = 314 from Part 1. | [6 empty] | Using Fig 10-13 to find J Factor using NR = 314 from Part 1.
J |  |  |  | = | 1900 |  | J |  |  |  | = | 1900
ht | = | (1900 • 0.12 • 0.96)/0.87 |  | = | 251.5862 |  | ht | = | (1900 • 0.12 • 0.96)/0.87 |  | = | 251.5862
12. Calculate Air Quantity | [6 empty] | 12. Calculate Air Quantity
Wa | = | 15000000/(0.24 • 52) |  | = | 1201923.0769 | lb/hr | Wa | = | 15000000/(0.24 • 52) |  | = | 1201923.0769 | lb/hr
13. Calculate Air Face Mass Velocity | [6 empty] | 13. Calculate Air Face Mass Velocity
Ga | = | 1201923/465 |  | = | 2584.7808 | lb/hr-sq.ft. face area | Ga | = | 1201923/465 |  | = | 2584.7808 | lb/hr-sq.ft. face area
14. Read Air-Side Film Coefficient from Fig 10-17 | [6 empty] | 14. Read Air-Side Film Coefficient from Fig 10-17
ha |  |  |  | = | 8.5 | Btu/(hr-degF-ft2) | ha |  |  |  | = | 8.5 | Btu/(hr-degF-ft2)
15. Calculate Overall Transfer Coefficient | [6 empty] | 15. Calculate Overall Transfer Coefficient
Ax/Ai | = | (21.4 • 1.0)/0.87 |  | = | 24.5977 |  | Ax/Ai | = | (21.4 • 1.0)/0.87 |  | = | 24.5977
1/Ux | = | [(1/252) • 24.6] + (0.001 • 24.6) + (1/8.5) |  | = | 0.24002 |  | 1/Ux | = | [(1/252) • 24.6] + (0.001 • 24.6) + (1/8.5) |  | = | 0.24002
|  | Note: rmx is ommitted since metal resistance is small compared to other resistances | [6 empty] | Note: rmx is ommitted since metal resistance is small compared to other resistances
Ux | = | 1/0.240 |  | = | 4.1664 | Btu/(h • ft2 • °F) | Ux | = | 1/0.240 |  | = | 4.1664 | Btu/(h • ft2 • °F)
|  | If Ux calculated is equal or slightly greater than Ux assumed at beginning and calculated pressure drop is within allowable pressure drop then the solution is acceptable. Otherwise repeat steps 1-15 assuming a new Ux between original assumed value and calculated value | [6 empty] | If Ux calculated is equal or slightly greater than Ux assumed at beginning and calculated pressure drop is within allowable pressure drop then the solution is acceptable. Otherwise repeat steps 1-15 assuming a new Ux between original assumed value and calculated value
16. Calculate Minimum Fan Area | [6 empty] | 16. Calculate Minimum Fan Area
FAPF | = | (0.4 • 465)/2 |  | = | 93 | ft2 | FAPF | = | (0.4 • 465)/2 |  | = | 93 | ft2
17. Calculate Fan Diameter | [6 empty] | 17. Calculate Fan Diameter
D | = | [(4 • 93)/π]0.5 |  | = | 11 | ft | D | = | [(4 • 93)/π]0.5 |  | = | 11 | ft
18. Calculate Air Static Pressure Drop | [6 empty] | 18. Calculate Air Static Pressure Drop
Ta, avg | = | (100+152)/2 |  | = | 126 | °F | Ta, avg | = | (100+152)/2 |  | = | 126 | °F
Use Fig 10-18 to find Fp using Ga | [6 empty] | Use Fig 10-18 to find Fp using Ga
Fp |  |  |  | = | 0.1 | in. H2O/row of tubes | Fp |  |  |  | = | 0.1 | in. H2O/row of tubes
Use Fig 10-16 to find DR using Ta, avg | [6 empty] | Use Fig 10-16 to find DR using Ta, avg
DR |  |  |  | = | 0.94 |  | DR |  |  |  | = | 0.94
ΔPa | = | (0.1 • 4)/0.94 |  | = | 0.42553 | in. H2O | ΔPa | = | (0.1 • 4)/0.94 |  | = | 0.42553 | in. H2O
19. Calculate Actual Air Volume using DR of Air at Fan Inlet | [6 empty] | 19. Calculate Actual Air Volume using DR of Air at Fan Inlet
ACFM | = | 1201923/(0.94 • 60 • 0.0749) |  | = | 22670.9498 | Total | ACFM | = | 1201923/(0.94 • 60 • 0.0749) |  | = | 22670.9498 | Total
|  |  |  | = | 11335.4749 | per Fan |  |  |  |  | = | 11335.4749 | per Fan
20. Approximate Fan Total Pressure using DR of Air at Fan and Fan Area | [6 empty] | 20. Approximate Fan Total Pressure using DR of Air at Fan and Fan Area
PF | = | 0.43 + [142261/(4005 • ((π • 112)/4))]2 • 0.94 |  | = | 0.42637 | in. H2O | PF | = | 0.43 + [142261/(4005 • ((π • 112)/4))]2 • 0.94 |  | = | 0.42637 | in. H2O
21. Approximate Brake Horsepower Per Fan, using 70% Fan Efficiency | [6 empty] | 21. Approximate Brake Horsepower Per Fan, using 70% Fan Efficiency
Fan Efficiency |  |  |  | = | 0.7 |  | Fan Efficiency |  |  |  | = | 0.7
bhp | = | (142261 • 0.56)/(6356 • 0.7) |  | = | 1.0863 |  | bhp | = | (142261 • 0.56)/(6356 • 0.7) |  | = | 1.0863
Actual Fan Motor needed for 92% Efficient Speed reducer | [6 empty] | Actual Fan Motor needed for 92% Efficient Speed reducer
|  |  |  | = | 0.92 | [5 empty] | = | 0.92
bhp | = | 17.81/0.92 |  | = | 1.1807 | hp | bhp | = | 17.81/0.92 |  | = | 1.1807 | hp
|  |  |  | = | 2 | hp |  |  |  |  | = | 2 | hp
Calculate Extended Surface Area | [6 empty] | Calculate Extended Surface Area
A | = | 15.5 • 30 |  | = | 465 | ft2 | A | = | 15.5 • 30 |  | = | 465 | ft2
A | = | 465 • 107.2 |  | = | 49848 | ft2 | A | = | 465 • 107.2 |  | = | 49848 | ft2
One Unit having | [6 empty] | One Unit having
| 49848 | ft2 of extended area | [5 empty] | 49848 | ft2 of extended area
| 11 | ft diameter fans | [5 empty] | 11 | ft diameter fans
| 2 | hp fan drivers | [5 empty] | 2 | hp fan drivers
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Limits
LIMITS
Limit air out temp to 200 degF. Prevent damaging fan blades, bearings, V-belts.
Use forced air fan for process fluids above 350 degF. Prevent fan blade and bearing failure.
Angle condensing surfaces to allow positive drainage.
Fan size ranges from 3 to 28 ft. diameter.
Limit fan tip air speed to 12,000 fpm.
Use V-belt drives up to about 30 bhp. Gear drives above 30 bhp.
Limit driver size to 50 bhp.
Use tension wrapped finned tubes for service below 400 deg F process fluid.
Air face velocity is typically 600 SCF/min.
For warm air recirculation, keep air flow below 500 ft/min.
Truck shippable air coolers do not exceed typically 15 ft X 45 ft
Avoid placing bank of coolers downwind from other heat gererating equipment.
Normally, the bank should be oriented such that the wind flows parallel to the long axis of the bank of coolers.