## Fig 11-1 - Nomenclature
FIG. 11-1
Nomenclature
Acfm | = | actual volumetric flow rate of air-vapor mixture, cu ft/min | lba | = | pounds of dry air
ahp | = | air horsepower, hp | lbw | = | pounds of water
AWB | = | ambient wet bulb temperature, °F | L | = | water rate, lb/(sq ft • hr)
B | = | combined water loss through blowdown and windage, % of circulating water or cu ft/min | LG | = | liquid to gas ratio, lb/lb
CWT | = | cold water temperature, °F | Q | = | cu ft/min
DB | = | dry bulb temperature, °F | PF |  | performance factor, dimensionless
E | = | water evaporated, % of circulating water or cu ft/min | R |  | cooling tower range, °F
gpm | = | gallons per minute | V |  | air velocity, ft/min
G | = | air rate, lb/(sq ft • hr) | va | = | specific volume of dry air, cu ft/lb
ha | = | specific enthalpy of dry air, BTU/lb | vas | = | vs - va, cu ft/lb
has | = | hs - ha, BTU/lb | vs | = | volume of moist air at saturation per lb of dry air, cu ft/lb
hs | = | enthalpy of moist air at saturation per lb of dry air, BTU/lb | Ws | = | lbw/lba, humidity ratio at saturation
HWT | = | hot water temperature, °F | WB | = | wet bulb temperature, °F
Air Horsepower | = | The power output developed by a fan in moving a given air rate against a given resistance. | Fan Deck | = | Surface enclosing the top of an induced draft cooling tower, exclusive of the distribution basins on a crossflow tower.
Air Inlet | = | Opening in a cooling tower through which air enters. Sometimes referred to as the louvered face on induced draft towers. | Fan Pitch | = | The angle which the blades of a propeller fan make with the plane of rotation, measured at a prescribed point on each blade.
Air Rate | = | Mass flow of dry air per square foot of cross-sectional area in the tower's heat transfer region per hour. | Fill | = | That portion of a cooling tower which constitutes its primary heat transfer surface. Sometimes referred to as "packing."
Air Velocity | = | Velocity of air-vapor mixture through a specific region of the tower (i.e. the fan). | Forced Draft | = | Refers to the movement of air under pressure through a cooling tower. Fans of forced draft towers are located at the air inlets to "force" air through the tower.
Ambient Wet-Bulb Temperature | = | The wet-bulb temperature of the air encompassing a cooling tower, not including any temperature contribution by the tower itself. Generally measured upwind of a tower, in a number of locations sufficient to account for all extraneous sources of heat. | Hot Water Temperature | = | Temperature of circulating water entering the cooling tower's distribution system.
Approach | = | Difference between the cold water temperature and the entering wet-bulb temperature. | Induced Draft | = | Refers to the movement of air through a cooling tower by means of an induced partial vacuum. Fans of induced draft towers are located at the air discharges to "draw" air through the tower.
Blowdown | = | Water discharged from the system to control concentrations of salt or other impurities in the circulating water. | Liquid-to-Gas Ratio | = | A ratio of the total mass flows of water and dry air in a cooling tower. (See Air Rate and Water Rate)
Capacity | = | The amount of water that a cooling tower will cool through a specified range, at a specified approach and wet-bulb temperature. | Louvers | = | Blade or passage type assemblies installed at the air inlet face of a cooling tower to control water splashout and/or promote uniform air flow through the fill. In the case of film-type crossflow fill, they may be integrally molded to the film sheets.
Cell | = | Smallest tower subdivision which can function as an independent unit with regard to air and water flow; it is bounded by either exterior walls or partition walls. Each cell may have one or more fans and one or more distribution systems. | Makeup | = | Water added to the circulating water system to replace water lost by evaporation, drift, windage, blowdown, and leakage.
Circulation Rate | = | Actual water flow rate through a given tower. | Natural Draft | = | Refers to the movement of air through a cooling tower purely by natural means. Typically, by the driving force of a density differential.
Cold Water Temperature | = | Temperature of the water leaving the collection basin, exclusive of any temperature effects incurred by the addition of makeup and/or the removal of blowdown. | Net Effect Volume | = | That portion of the total structural volume within which the circulating water is in intimate contact with the flowing air.
Collection Basin | = | Chamber below and integral with the tower where water is transiently collected and directed to the sump or pump suction line. | Performance Factor | = | Variable used in determining performance characteristics inn cooling towers.
Counterflow | = | Air flow direction through the fill is counter-current to that of the falling water. | Psychrometer | = | An instrument incorporating both a dry-bulb and a wet-bulb thermometer, by which simultaneous dry-bulb and wet-bulb temperature readings can be taken.
Crossflow | = | Air flow direction through the fill is essentially perpendicular to that of the falling water. | Range | = | Difference between the hot water temperature and the cold water temperature.
Distribution Basin | = | Shallow pan-type elevated basin used to distribute hot water over the tower fill by means of orifices in the basin floor. Application is normally limited to crossflow towers. | Recirculation | = | Describes a condition in which a portion of the tower's discharge air re-enters the air inlets along with the fresh air. Its effect is an elevation of the average entering wet-bulb temperature compared to the ambient.
Double-Flow | = | A crossflow cooling tower where two opposed fill banks are served by a common air plenum. | Water Rate | = | Mass flow of water per square foot of fill plan area of the cooling tower per hour.
Drift | = | Circulating water loss from the tower as liquid droplets entrained in the exhaust air stream. Units percent of circulating water rate or gpm. [For more precise work, an L/G parameter is used, and drift becomes pounds of water per million pounds of exhaust air (ppmw).] | Wet-Bulb Temperature | = | The temperature of the entering or ambient air adjacent to the cooling tower as measured with a wet-bulb thermometer.
Drift Eliminators | = | An assembly of baffles or labyrinth passages through which the air passes prior to its exit from the tower, for the purpose of removing entrained water droplets from the exhaust air. | Wet-Bulb Thermometer | = | A thermometer whose bulb is encased within a wetted wick.
Dry-Bulb Temperature | = | The temperature of the entering or ambient air adjacent to the cooling tower as measured with a dry-bulb thermometer. | Windage | = | Water lost from the tower because of the effects of wind.
Evaporation Loss | = | Water evaporated from the circulating water into the air stream in the cooling process. | Wind Load | = | The load imposed upon a structure by a wind blowing against its surface.
Fan Cylinder | = | Cylindrical or venturi-shaped structure in which a propeller fan operates. Sometimes referred to as a fan "stack" on larger towers.
KEY
| = | Example calculation from the book
| = | Application worksheet for user to fill out
| = | Numbers that must be filled in according to the user's data and specific situation
| = | Numbers that must be filled in according to graphs and charts

## Example 11-1
Example 11-1 -- Effect of Varying WB Temperature on Cold Water Temperature (CWT) |  |  |  |  | Application 11-1 -- Effect of Varying WB Temperature on Cold Water Temperature (CWT)
Given Data: |  |  |  |  | Given Data:
Flow | = | 1000 | gpm |  | Flow | = | 1000 | gpm
Hot Water | = | 105 | °F |  | Hot Water | = | 105 | °F
Cold Water | = | 85 | °F |  | Cold Water | = | 85 | °F
Wet Bulb | = | 75 | °F |  | Wet Bulb | = | 75 | °F
This is commonly referred to as 20° Range (105-85) and 10° Approach (85-75). |  |  |  |  | This is commonly referred to as 20° Range (105-85) and 10° Approach (85-75).
What is the new CWT when WB changes from |  |  |  |  | What is the new CWT when WB changes from
| 75 | ° to | 60 | ° with |  |  | 75 | ° to | 60 | ° with
gpm and range remaining constant? |  |  |  |  | gpm and range remaining constant?
Enter Nomograph at 85° CWT, go horizontally to 75° WB, then vertically down to 60° WB, read new CWT of |  |  |  |  | Enter Nomograph at 85° CWT, go horizontally to 75° WB, then vertically down to 60° WB, read new CWT of
| 76 | °. |  |  |  | 76 | °.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 11-2
Example 11-2 -- Effect of Varying Cooling Range on Cold Water Temperature |  |  |  |  | Application 11-2 -- Effect of Varying Cooling Range on Cold Water Temperature
Given Data: |  |  |  |  | Given Data:
Flow | = | 1000 | gpm |  | Flow | = | 1000 | gpm
Hot Water | = | 105 | °F |  | Hot Water | = | 105 | °F
Cold Water | = | 85 | °F |  | Cold Water | = | 85 | °F
Wet Bulb | = | 75 | °F |  | Wet Bulb | = | 75 | °F
What is the new CWT when cooling range is changed from |  |  |  |  | What is the new CWT when cooling range is changed from
| 20 | ° to | 30 | °? |  | 20 | ° to | 30 | °?
(50% increase in heat load) with gpm and WB held constant? |  |  |  |  | (50% increase in heat load) with gpm and WB held constant?
Enter Nomograph at 85° CWT, go horizontally to 75° WB, vertically to R = 20° F, horizontally to R = 30° F, vertically downward to 75° WB, read new CWT of |  |  |  |  | Enter Nomograph at 85° CWT, go horizontally to 75° WB, vertically to R = 20° F, horizontally to R = 30° F, vertically downward to 75° WB, read new CWT of
| 87.5 | °. |  |  |  | 87.5 | °.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 11-3
Example 11-3 -- Effect of Varying Water Circulating Rate and Heat Load on | [6 empty] | Application 11-3 -- Effect of Varying Water Circulating Rate and Heat Load on
Cold Water Temperature | [6 empty] | Cold Water Temperature
Given Data: | [6 empty] | Given Data:
Flow | = | 1000 | gpm |  |  |  | Flow | = | 1000 | gpm
Hot Water | = | 105 | °F |  |  |  | Hot Water | = | 105 | °F
Cold Water | = | 85 | °F |  |  |  | Cold Water | = | 85 | °F
Wet Bulb | = | 75 | °F |  |  |  | Wet Bulb | = | 75 | °F
What is the new CWT when water circulation is changed from |  |  |  | 1000 | gpm to | 1500 | What is the new CWT when water circulation is changed from |  |  |  | 1000 | gpm to | 1500
gpm (50% change in heat load at constant Range). | [6 empty] | gpm (50% change in heat load at constant Range).
Varying water rate, particularly over wide ranges, may require modifications to the distribution system. Enter Nomograph at 85° CWT, go horizontally to 75° WB, vertically to R = 20° F, horizontally to Performance Factor of | [6 empty] | Varying water rate, particularly over wide ranges, may require modifications to the distribution system. Enter Nomograph at 85° CWT, go horizontally to 75° WB, vertically to R = 20° F, horizontally to Performance Factor of
3.1 | . | [5 empty] | 3.1 | .
Obtain new PF by multiplying (3.1)(1500/1000) = 4.65, then enter Nomograph at PF of 4.65, go horizontally to R = 20° F, vertically down to 75° WB, read new CWT of | [6 empty] | Obtain new PF by multiplying (3.1)(1500/1000) = 4.65, then enter Nomograph at PF of 4.65, go horizontally to R = 20° F, vertically down to 75° WB, read new CWT of
| 90.5° | . | [5 empty] | 90.5 | °.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 11-4
Example 11-4 -- Effect of Varying WB Temperature, Range, and Water Circulating Rate on | [6 empty] | Application 11-4 -- Effect of Varying WB Temperature, Range, and Water Circulating Rate on
Cold Water Temperature | [6 empty] | Cold Water Temperature
Given Data: | [6 empty] | Given Data:
Flow | = | 1000 | gpm |  |  |  | Flow | = | 1000 | gpm
Hot Water | = | 105 | °F |  |  |  | Hot Water | = | 105 | °F
Cold Water | = | 85 | °F |  |  |  | Cold Water | = | 85 | °F
Wet Bulb | = | 75 | °F |  |  |  | Wet Bulb | = | 75 | °F
What is the new CWT when the WB changes from |  |  |  | 75 | ° to | 60 | What is the new CWT when the WB changes from |  |  |  | 75 | ° to | 60
°, R changes from | 20 | ° F to | 25 | ° F, and gpm changes from |  | 1000 | °, R changes from | 20 | ° F to | 25 | ° F, and gpm changes from |  | 1000
to | 1250 | (25% change in heat load). |  |  |  |  | to | 1250 | (25% change in heat load).
Enter Nomograph at 85° CWT, go horizontally to 75° WB, vertically to R = 20° F, horizontally read PF = | [6 empty] | Enter Nomograph at 85° CWT, go horizontally to 75° WB, vertically to R = 20° F, horizontally read PF
3.1 | [6 empty] | 3.1
then multiply (3.1)(1250/1000) = 3.88 (new PF). Enter Nomograph at PF = 3.88, go horizontally to R = 25° F, vertically down to 60° WB, read new CWT of | [6 empty] | then multiply (3.1)(1250/1000) = 3.88 (new PF). Enter Nomograph at PF = 3.88, go horizontally to R = 25° F, vertically down to 60° WB, read new CWT of
| 82 | °. | [5 empty] | 82 | °.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 11-5
Example 11-5 -- Effect of Varying Fan HP Input on Cold Water Temperature | [6 empty] | Application 11-5 -- Effect of Varying Fan HP Input on Cold Water Temperature
Given Data: | [6 empty] | Given Data:
Flow | = | 1000 | gpm |  |  |  | Flow | = | 1000 | gpm
Hot Water | = | 105 | °F |  |  |  | Hot Water | = | 105 | °F
Cold Water | = | 85 | °F |  |  |  | Cold Water | = | 85 | °F
Wet Bulb | = | 75 | °F |  |  |  | Wet Bulb | = | 75 | °F
What is the new CWT if motor is changed from |  |  |  | 20 | HP to | 25 | What is the new CWT if motor is changed from |  |  |  | 20 | HP to | 25
HP in Example 11-4? Example 11-4 information given below: | [6 empty] | HP in Example 11-4? Example 11-4 information given below:
WB change: | 75 | to | 60 |  |  |  | WB change: | 75 | to | 60
R change: | 20 | to | 25 |  |  |  | R change: | 20 | to | 25
GPM change: | 1000 | to | 1250 |  |  |  | GPM change: | 1000 | to | 1250
Original PF: | 3.1 | (see previous example for how to get this value) |  |  |  |  | Original PF: | 3.1 | (see previous example for how to get this value)
The air flow rate varies as the cube root of the horsepower and performance varies almost directly with the ratio of water rate to air rate, therefore the change in air flow rate can be applied to the Performance Factor. Increasing the air flow rate (by installing a larger motor) decreases the Performance Factor. | [6 empty] | The air flow rate varies as the cube root of the horsepower and performance varies almost directly with the ratio of water rate to air rate, therefore the change in air flow rate can be applied to the Performance Factor. Increasing the air flow rate (by installing a larger motor) decreases the Performance Factor.
PF correction factor = (25 HP/20 HP)^(1/3) = 1.077. Divide PF by PF correction factor to get new PF. Applying this to Example 11-4, we get 3.875/1.077 = 3.6. Enter Nomograph at 3.6 PF (instead of 3.88 PF) go horizontally to R =25° F, vertically down to 60° WB, read CWT of | [6 empty] | PF correction factor = (25 HP/20 HP)^(1/3) = 1.077. Divide PF by PF correction factor to get new PF. Applying this to Example 11-4, we get 3.875/1.077 = 3.6. Enter Nomograph at 3.6 PF (instead of 3.88 PF) go horizontally to R = 25° F, vertically down to 60° WB, read CWT of
| 81 | °. | [5 empty] | 81 | °.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 11-6
Example 11-6 -- Effect of correction factor on gpm instead of Cold Water Temperature | [6 empty] | Application 11-6 -- Effect of correction factor on gpm instead of Cold Water Temperature
Given Data: | [6 empty] | Given Data:
Flow | = | 1000 | gpm |  |  |  | Flow | = | 1000 | gpm
Hot Water | = | 105 | °F |  |  |  | Hot Water | = | 105 | °F
Cold Water | = | 85 | °F |  |  |  | Cold Water | = | 85 | °F
Wet Bulb | = | 75 | °F |  |  |  | Wet Bulb | = | 75 | °F
Use the PF correction factor from Example 11-5 to increase gpm instead of decreasing CWT. | [6 empty] | Use the PF correction factor from Example 11-5 to increase gpm instead of decreasing CWT.
Example 11-5: | [6 empty] | Example 11-5:
What is the new CWT if motor is changed from |  |  |  | 20 | HP to | 25 | What is the new CWT if motor is changed from |  |  |  | 20 | HP to | 25
HP in Example 11-4? Example 11-4 information given below: | [6 empty] | HP in Example 11-4? Example 11-4 information given below:
WB change: | 75 | to | 60 |  |  |  | WB change: | 75 | to | 60
R change: | 20 | to | 25 |  |  |  | R change: | 20 | to | 25
GPM change: | 1000 | to | 1250 |  |  |  | GPM change: | 1000 | to | 1250
Original PF: | 3.1 | (see example 11-4 for how to get this value) |  |  |  |  | Original PF: | 3.1 | (see example 11-4 for how to get this value)
In Example 11-4, we developed a new CWT of 82 when circulating 1250 gpm at R = 25° F and 60° WB. If motor HP is increased from 20 to 25 under these conditions with PF correction factor = 1.077 (as shown in Example 11-5), GPM could be increased from 1250 to (1250)(1.077) = | [6 empty] | In Example 11-4, we developed a new CWT of 82° when circulating 1250 gpm at R = 25° F and 60° WB. If motor HP is increased from 20 to 25 under these conditions with PF correction factor = 1.077 (as shown in Example 11-5), GPM could be increased from 1250 to (1250)(1.077) =
| 1347 | gpm. | [5 empty] | 1346.5217 | gpm.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 11-7
Example 11-7 -- Cooling tower calculations on concentration and blowdown rate | [6 empty] | Application 11-7 -- Cooling tower calculations on concentration and blowdown rate
Calculate the concentrations and blowdown rate for the following cooling tower: | [6 empty] | Calculate the concentrations and blowdown rate for the following cooling tower:
Circulation Rate | = | 10000 | gpm |  |  |  | Circulation Rate | = | 10000 | gpm
Water Temperature Drop Through Tower | = | 20 | °F |  |  |  | Water Temperature Drop Through Tower | = | 20 | °F
Type of Tower | = | Mechanical-draft towers |  |  |  |  | Type of Tower | = | Mechanical-draft towers
Blowdown Rate | = | 20 | gpm |  |  |  | Blowdown Rate | = | 20 | gpm
| or | 0.2% | of circulation rate |  |  |  |  | or | 0.2% | of circulation rate
Therefore: | [6 empty] | Therefore:
Evaporation Loss | = | 2% | (1% for each 10° temperature drop) |  |  |  | Evaporation Loss | = | 2% | (1% for each 10° temperature drop)
Windage Loss | = | 0.3% | (Maximum for mechanical draft tower, p. 11-9) |  |  |  | Windage Loss | = | 0.3% | Maximum for Mechanical-draft towers, p. 11-9
Number of Concentrations (cycles) |  | = | (E + B) / B = |  |  |  | Number of Concentrations (cycles) |  | = | (E + B) / B =
| (0.02 + (0.002 + 0.003))/(0.002 + 0.003) |  |  | = | 5 |  |  | (0.02 + (0.002 + 0.003))/(0.002 + 0.003) |  |  | = | 5
If the resultant concentrations are excessive and a desired concentration of | [5 empty] | 4 | If the resultant concentrations are excessive and a desired concentration of | [5 empty] | 4
is required, what must the blowdown rate be? | [6 empty] | is required, what must the blowdown rate be?
B = E / (Cycles - 1) | = | 0.6667% |  |  |  |  | B = E / (Cycles - 1) | = | 0.6667%
The windage component of B is 0.003, therefore the blowdown rate required would be 0.0067 - 0.003 = 0.0037 or | [6 empty] | The windage component of B is 0.003, therefore the blowdown rate required would be 0.0067 - 0.003 = 0.0037 or
| (10000 gpm) (0.0037) = | [6 empty] | (10000 gpm) (0.0037) =
|  | 37 | gpm. | [5 empty] | 36.6667 | gpm.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.