## FIG. 14-1 Nomenclature
FIG. 14-1
Nomenclature
GHP | = | gas horsepower defined by Eq 14-7b | Subscripts
h | = | enthalpy, Btu/lb | L | = | liquid state
h'vd | = | isentropic enthalpy Btu/lb | V | = | vapor state
k | = | specific heat ratio | A,B,C,D | = | denote unique points of operation on P-H diagrams
m | = | refrigerant flow, lb/hr | b | = | bypass
n | = | number of stages | i | = | isentropic
P | = | pressure, psia | cd | = | condenser
Q | = | heat duty, BTU/hr | ref | = | refrigeration
r | = | compression ratio | s | = | suction
S | = | entropy, Btu/(lb-°R) | d | = | discharge
T | = | temperature, °F | n | = | stage number
W | = | work of compression, Btu/hr | T | = | Total
X | = | weight fraction | 1,2 | = | stage number
h | = | isentropic efficiency
s | = | surface tension, dynes/cm
r | = | density, lb/ft3
Dh | = | enthalpy change, Btu/lb

## Limits
Limits from the 13th Edition of the Data Book
Refrigerant Condensing Temperatures
Refrigerant
Condensing
Temperature
| Heat Sink | F
| Water | 80-100
| Air (Gulf Coast) | 115-125
Lowest Refrigerant Temperatures near Atmospheric Pressure
Temperature
| Refrigerant | F
| Ethane | -120
| Propane | -40
Use double-acting packing on cylinders operating near or below atmospheric pressure.
The refrigerant system should be designed for at least 250 psig throughout.
This is due to the vapor pressure of the refrigerant at ambient temperatures whe the system is down.
Be aware of metallurgical cold temperature limits (eg, -20F for carbon steel).
Refer to ANSI B31.3 and ANSI B31.5 (Refrigeration Piping Code)
The lowest operating temperature for a lithium bromide-water system is 42F.
Units typically operate between 42F and 50F.

## Example 14-1
Example 14-1 -- Calculate the horsepower and condenser duty required for the process shown in Fig 14-8 using propane refrigeration. Design condensing temperature is 120 °F. The pressure drop from the chillers to the compressor suction is 1.5 psi. The pressure drop from compressor discharge to the receiver is 10 psi. | [6 empty] | Example 14-1 -- Calculate the horsepower and condenser duty required for the process shown in Fig 14-8 using propane refrigeration. Design condensing temperature is 120 °F. The pressure drop from the chillers to the compressor suction is 1.5 psi. The pressure drop from compressor discharge to the receiver is 10 psi.
Given Data: | [6 empty] | Given Data:
Chiller 1 Temperature T1 | = | -40 | °F |  |  |  | Chiller 1 Temperature T1 | = | -40 | °F
Chiller 1 Duty Q1 | = | 25 | MMBtu/hr |  |  |  | Chiller 1 Duty Q1 | = | 25 | MMBtu/hr
Chiller 2 Temperature T2 | = | 25 | °F |  |  |  | Chiller 2 Temperature T2 | = | 25 | °F
Chiller 2 Duty Q2 | = | 10 | MMBtu/hr |  |  |  | Chiller 2 Duty Q2 | = | 10 | MMBtu/hr
Receiver Temperature TR | = | 120 | °F | = | 579.67 | °R | Receiver Temperature TR | = | 120 | °F | = | 579.67 | °R
Pressure Drop between compressor and receiver DP1 | = | 10 | psi |  |  |  | Pressure Drop between compressor and receiver DP1 | = | 10 | psi
Presure drop between chillers and compressor suction DP2 | = | 1.5 | psi |  |  |  | Presure drop between chillers and compressor suction DP2 | = | 1.5 | psi
Propane Vapor Pressure at 120 F (from curve) P*120 | = | 240 | psia |  |  |  | Propane Vapor Pressure at 120 F (from curve) P*120 | = | 240 | psia
Propane Vapor Pressure at -40 F (from curve) P*-40 | = | 16 | psia |  |  |  | Propane Vapor Pressure at -40 F (from curve) P*-40 | = | 16 | psia
Liquid Enthalpy @ 120 F, 240 psia (from curve) hL2 | = | 325 | Btu/lb |  |  |  | Liquid Enthalpy @ 120 F, 240 psia (from curve) hL2 | = | 325 | Btu/lb
Liquid Enthalpy @ 25 F, 62 psia (from curve) hL1 | = | 265 | Btu/lb |  |  |  | Liquid Enthalpy @ 25 F, 62 psia (from curve) hL1 | = | 265 | Btu/lb
Vapor Enthalpy @ 25 F, 62 psia (from curve) hV2 | = | 425 | Btu/lb |  |  |  | Vapor Enthalpy @ 25 F, 62 psia (from curve) hV2 | = | 425 | Btu/lb
Vapor Enthalpy @ -40 F, 16 psia (from curve) hV1 | = | 405 | Btu/lb |  |  |  | Vapor Enthalpy @ -40 F, 16 psia (from curve) hV1 | = | 405 | Btu/lb
Isentropic Enthalpy at 60 psia (Figure 24-26) h'vd-60 | = | 440 | Btu/lb | based on inlet entropy of 0.93 Btu/(lb-R) |  |  | Isentropic Enthalpy at 60 psia (Figure 24-26) h'vd-60 | = | 440 | Btu/lb | based on inlet entropy of 0.93 Btu/(lb-R)
Isentropic Enthalpy at 250 psia (Figure 24-26) h'vd-250 | = | 465 | Btu/lb |  |  |  | Isentropic Enthalpy at 250 psia (Figure 24-26) h'vd-250 | = | 465 | Btu/lb
Isentropic Efficiency h | = | 0.75 |  |  |  |  | Isentropic Efficiency h | = | 0.75
To determine the HP of each stage, the work for each stage must be calculated | [6 empty] | To determine the HP of each stage, the work for each stage must be calculated
W | = | DHideal (m) / h |  |  |  | Eq. 14-7 | W | = | DHideal (m) / h |  |  |  | Eq. 14-7
GHP | = | W / 2,544.4 |  |  |  | Eq. 14-7b | GHP | = | W / 2544.4 |  |  |  | Eq. 14-7b
To determine the total HP, add the HP of each stage, | [6 empty] | To determine the total HP, add the HP of each stage,
Total HP | = | GHP1 + GHP2 |  |  |  |  | Total HP | = | GHP1 + GHP2
To determine the condesner duty, multiply the mass flow through the condenser by the enthalpy change in the condenser | [6 empty] | To determine the condesner duty, multiply the mass flow through the condenser by the enthalpy change in the condenser
Qcd | = | (hv2d - hL2)*mT |  |  |  | Eq. 14-8 | Qcd | = | (hv2d - hL2)*mT |  |  |  | Eq. 14-8
Intermediate Calculations | [6 empty] | Intermediate Calculations
To determine 1st stage suction pressure | [6 empty] | To determine 1st stage suction pressure
Ps | = | P*-40 - 1.5 psi | = | 14.5 | psia |  | Ps | = | P*-40 - 1.5 psi | = | 14.5 | psia
To determine 2nd stage discharge pressure | [6 empty] | To determine 2nd stage discharge pressure
Pd | = | P*120 + 10 psi | = | 250 | psia |  | Pd | = | P*120 + 10 psi | = | 250 | psia
To determine the compression ratio per stage | [6 empty] | To determine the compression ratio per stage
r | = | (Pd/Ps)1/n | = | 4.1523 |  |  | r | = | (Pd/Ps)1/n | = | 4.1523
To determine second stage suction pressure | [6 empty] | To determine second stage suction pressure
Ps2 | = | Psr | = | 60.208 | psia |  | Ps2 | = | Psr | = | 60.208 | psia
To determine 1st stage discharge pressure | [6 empty] | To determine 1st stage discharge pressure
Pd1 | = | Ps2 + 2.0 psi | = | 62.208 | psia |  | Pd1 | = | Ps2 + 2.0 psi | = | 62.208 | psia
To determine mass flow through Chiller #1 | [6 empty] | To determine mass flow through Chiller #1
m1 | = | Q1/(hv1-hL1) | = | 178571.4286 | lb/hr |  | m1 | = | Q1/(hv1-hL1) | = | 178571.4286 | lb/hr
To determine mass flow through Chiller #2 | [6 empty] | To determine mass flow through Chiller #2
m2 | = | Q2/(hv2-hL2) | = | 100000 | lb/hr |  | m2 | = | Q2/(hv2-hL2) | = | 100000 | lb/hr
By performing a heat balance around the second stage suction drum, referring to Fig. 14-9 | [6 empty] | By performing a heat balance around the second stage suction drum, referring to Fig. 14-9
[mb - (m1-m2)] (hV2) + m1 (hL1) | = | mb (hL2) + m2 (hV2) |  |  |  |  | [mb - (m1-m2)] (hV2) + m1 (hL1) | = | mb (hL2) + m2 (hV2)
mb | = |  | = | 285714.2857 | lb/hr |  | mb | = |  | = | 285714.2857 | lb/hr
To determine ideal change in enthalpy across first stage: | [6 empty] | To determine ideal change in enthalpy across first stage:
DHideal1 | = | h'vd-60 - 410 | = | 30 | Btu/lb |  | DHideal1 | = | h'vd-60 - 410 | = | 30 | Btu/lb
To determine 1st stage horsepower | [6 empty] | To determine 1st stage horsepower
GHP1 | = | DHideal1(m1)/(2,544.4 * h) | = | 2807.2855 | hp |  | GHP1 | = | DHideal1(m1)/(2544.4 * h) | = | 2807.2855 | hp
To determine 1st stage discharge enthalpy | [6 empty] | To determine 1st stage discharge enthalpy
hv1d | = | DHideal1/h + 410 | = | 450 | Btu/lb |  | hv1d | = | DHideal1/h + 410 | = | 450 | Btu/lb
By performing a material balance around the second stage compression, | [6 empty] | By performing a material balance around the second stage compression,
mT | = | m1 + (mb - 78,570) | = | 385714.2857 | lb/hr |  | mT | = | m1 + (mb - 78,570) | = | 385714.2857 | lb/hr
To determine 2nd stage inlet enthalpy | [6 empty] | To determine 2nd stage inlet enthalpy
hv2s | = | [(hv1d) (m1) + (hV2) (mb - 78,570)] / mT | = | 436.5741 | Btu/lb |  | hv2s | = | [(hv1d) (m1) + (hV2) (mb - 78570)] / mT | = | 436.5741 | Btu/lb
To determine ideal change in enthalpy across second stage: | [6 empty] | To determine ideal change in enthalpy across second stage:
DHideal2 | = | h'vd-250 - hv2s | = | 28.4259 | Btu/lb |  | DHideal2 | = | h'vd-250 - hv2s | = | 28.4259 | Btu/lb
To determine 2nd stage horsepower | [6 empty] | To determine 2nd stage horsepower
GHP2 | = | DHideal2 (mT) / (2544.4 * h) | = | 5745.5776 | hp |  | GHP2 | = | DHideal2 (mT) / (2544.4 * h) | = | 5745.5776 | hp
Total HP | = | GPH1 + GPH2 | = | 8552.8631 | hp |  | Total HP | = | GPH1 + GPH2 | = | 8552.8631 | hp
To determine 2nd stage discharge enthalpy | [6 empty] | To determine 2nd stage discharge enthalpy
hv2d | = | DHideal2/h + 437 | = | 474.4753 | Btu/lb |  | hv2d | = | DHideal2/h + 437 | = | 474.4753 | Btu/lb
To determine condenser duty | [6 empty] | To determine condenser duty
Qcd | = | (hv2d - hL2)*mT | = | 57.6548 | MMBtu/hr |  | Qcd | = | (hv2d - hL2)*mT | = | 57.6548 | MMBtu/hr
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 14-2
Example 14-2 -- Consider installing a 3 MMBtu/hr subcooler on the liquid propane refrigerant from the receiver at 120 F in Example 14-1 for the two-stage propane refrigeration system. The second stage of this system is shown in Figure 14-11. | [6 empty] | Example 14-2 -- Consider installing a 3 MMBtu/hr subcooler on the liquid propane refrigerant from the receiver at 120 F in Example 14-1 for the two-stage propane refrigeration system. The second stage of this system is shown in Figure 14-11.
Given Data: | [6 empty] | Given Data:
Figure 14-11 | = | see figure |  |  |  |  | Figure 14-11 | = | see figure
Subcooler Duty | = | 3 | MMBtu/hr |  |  |  | Subcooler Duty | = | 3 | MMBtu/hr
Second Stage Chiller Duty Q2 | = | 10 | MMBtu/hr |  |  |  | Second Stage Chiller Duty Q2 | = | 10 | MMBtu/hr
Receiver Temperature TR | = | 120 | °F | = | 579.67 | °R | Receiver Temperature TR | = | 120 | °F | = | 579.67 | °R
Mass Flow Rate to Chiller #1 (from Ex 1) m1 | = | 178570 | lb/hr |  |  |  | Mass Flow Rate to Chiller #1 (from Ex 1) m1 | = | 178570 | lb/hr
Liquid Enthalpy at 120 F hL | = | 325 | Btu/lb |  |  |  | Liquid Enthalpy at 120 F hL | = | 325 | Btu/lb
Vapor Enthalpy at 25 F hV | = | 425 | Btu/lb |  |  |  | Vapor Enthalpy at 25 F hV | = | 425 | Btu/lb
Determine the new total refrigerant mass flow rate, and flow rate to the second stage chiller flow rate | [6 empty] | Determine the new total refrigerant mass flow rate, and flow rate to the second stage chiller flow rate
Intermediate Calculations | [6 empty] | Intermediate Calculations
By performing a total heat balance around the system in 14-11 | [6 empty] | By performing a total heat balance around the system in 14-11
(mT) (hL) + Q2 | = | (mT-m1) (hV) + m1(265) + Subcooler Duty |  |  |  |  | (mT) (hL) + Q2 | = | (mT-m1) (hV) + m1(265) + Subcooler Duty
mT | = |  | = | 355712 | lb/hr |  | mT | = |  | = | 355712 | lb/hr
By performing a total heat balance around the subcooler, the enthalpy after the subcooler is: | [6 empty] | By performing a total heat balance around the subcooler, the enthalpy after the subcooler is:
hL2 | = | (mT (hL) - 3(10^6))/mT | = | 316.5662 | Btu/lb |  | hL2 | = | (mT (hL) - 3(10^6))/mT | = | 316.5662 | Btu/lb
To determine the new flowrate to the second stage chiller, | [6 empty] | To determine the new flowrate to the second stage chiller,
m2 | = | Q2 (10^6) / (hv-hL2) | = | 92222.1761 | lb/hr |  | m2 | = | Q2 (10^6) / (hv-hL2) | = | 92222.1761 | lb/hr
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 14-3
Example 14-3 -- Estimate the horsepower and condenser duty requirements for a single-stage propylene refrigeration system that will provide 25MMbtu/hr of process chilling at a refrigerant level of -20 F. | [6 empty] | Example 14-3 -- Estimate the horsepower and condenser duty requirements for a single-stage propylene refrigeration system that will provide 25MMbtu/hr of process chilling at a refrigerant level of -20 F.
Given Data: | [6 empty] | Given Data:
Chiller Duty | = | 25 | MMBtu/hr |  |  |  | Chiller Duty | = | 25 | MMBtu/hr
Refrigerant Temperature TR | = | -20 | °F | = | 439.67 | °R | Refrigerant Temperature TR | = | -20 | °F | = | 439.67 | °R
Condenser Temperature (assume) Tcd | = | 100 | °F |  |  |  | Condenser Temperature (assume) Tcd | = | 100 | °F
Calculations | [6 empty] | Calculations
Refer to figure 14-17 | [6 empty] | Refer to figure 14-17
GHP | = | 222 hp per MMbtu / hr of refrigeration @ evaporator temperature of -20 F |  |  |  |  | GHP | = | 222 hp per MMbtu / hr of refrigeration @ evaporator temperature of -20 F
|  | & cond temperature of 100 F | [6 empty] | & cond temperature of 100 F
GHP | = | 222 (25) | = | 5550 | hp |  | GHP | = | 222 (25) | = | 5550 | hp
Qcd | = | 1.565 MMBtu /hr per MMbtu / hr of refrigeration @ evaporator temperature of -20 F |  |  |  |  | Qcd | = | 1.565 MMBtu /hr per MMbtu / hr of refrigeration @ evaporator temperature of -20 F
|  | & cond temperature of 100 F | [6 empty] | & cond temperature of 100 F
Qcd | = | 1.565 (25) | = | 39.125 | MMBtu/hr |  | Qcd | = | 1.565 (25) | = | 39.125 | MMBtu/hr
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.