## For nomenclature
Figure 18-1
Nomenclature
A = ampere | psia = pounds per square inch absolute
AC = alternating current | psig = pounds per square inch gauge
BD = blowdown, gpm | pAlk = log(1/ppmw of M alkalinity) (see Fig. 18-22)
DC = direct current | pCa = log (1/ppmw of Ca) (see Fig. 18-22)
E = voltage, volts | pHS = calculated pH at saturation with calcium carbonate
eff = efficiency, percent | PF = power factor, decimal
F = filtering rate, gpm | R = resistance, ohms
hp = horsepower | SSF = final suspended solids content, ppmw
I = current, amperes | SSI = initial suspended solids content, ppmw
kV = kilovolt | V = electromotive force, volts
kW = kilowatt | W = watt
kVA = kilovolt-ampere | ~ = frequency, Hertz
kVAR = reactive kilovolt-amperes, kilovar | σ = symbol for phase, usually preceded by a number
LHV = lower or net heating value, Btu/SCF
N.C. = normally closed
N.O. = normally open
ppmw = part per million by weight

## Example 18-1
Example 18-1. Water Analysis Calculation. | [5 empty] | Example 18-1. Water Analysis Calculation.
Given: | [5 empty] | Given:
Water Analysis Ion |  | ppmw | Units | MW | Equiv. Wt. | Water Analysis Ion |  | ppmw | Units | MW | Equiv. Wt.
Calcium (Ca+2) | = | 100.1 | ppmw | 40.08 | 20.04 | Calcium (Ca+2) | = | 100.1 | ppmw | 40.08 | 20.04
Magnesium Mg+2) | = | 20.4 | ppmw | 24.32 | 12.16 | Magnesium Mg+2) | = | 20.4 | ppmw | 24.32 | 12.16
Sodium (Na+1) | = | 12 | ppmw | 23 | 23 | Sodium (Na+1) | = | 12 | ppmw | 23 | 23
Bicarbonate (HCO3-1) | = | 366 | ppmw | 61.02 | 61.02 | Bicarbonate (HCO3-1) | = | 366 | ppmw | 61.02 | 61.02
Sulfate (SO4-2) | = | 48.1 | ppmw | 96.06 | 48.03 | Sulfate (SO4-2) | = | 48.1 | ppmw | 96.06 | 48.03
Chloride (Cl-1) | = | 7.1 | ppmw | 35.46 | 35.46 | Chloride (Cl-1) | = | 7.1 | ppmw | 35.46 | 35.46
Additional ions can be added to the above list, using Equiv. Wt. = MW divided by ionic valence. | [5 empty] | Additional ions can be added to the above list, using Equiv. Wt. = MW divided by ionic valence.
Solution Steps | [5 empty] | Solution Steps
Cations |  | MEQ/liter | Units |  | ppmw as CaCO3 | Cations |  | MEQ/liter | Units |  | ppmw as CaCO3
Ca+2 | = | 4.995 | milliequivalents/liter |  | 249.9503 | Ca+2 | = | 4.995 | milliequivalents/liter |  | 249.9503
Mg+2 | = | 1.6776 | milliequivalents/liter |  | 83.9487 | Mg+2 | = | 1.6776 | milliequivalents/liter |  | 83.9487
Na+1 | = | 0.52174 | milliequivalents/liter |  | 26.1078 | Na+1 | = | 0.52174 | milliequivalents/liter |  | 26.1078
Totals | = | 7.1944 | milliequivalents/liter |  | 360.0068 | Totals | = | 7.1944 | milliequivalents/liter |  | 360.0068
Anions | [5 empty] | Anions
HCO3-1 | = | 5.998 | milliequivalents/liter |  | 300.1416 | HCO3-1 | = | 5.998 | milliequivalents/liter |  | 300.1416
SO4-2 | = | 1.0015 | milliequivalents/liter |  | 50.1129 | SO4-2 | = | 1.0015 | milliequivalents/liter |  | 50.1129
Cl-1 | = | 0.20023 | milliequivalents/liter |  | 10.0193 | Cl-1 | = | 0.20023 | milliequivalents/liter |  | 10.0193
Totals | = | 7.1997 | milliequivalents/liter |  | 360.2738 | Totals | = | 7.1997 | milliequivalents/liter |  | 360.2738
Total hardness (Ca+2 + Mg+2) |  | = |  |  | 333.899 | Total hardness (Ca+2 + Mg+2) |  | = |  |  | 333.899
Total alkalinity (HCO3-1) |  | = |  |  | 300.1416 | Total alkalinity (HCO3-1) |  | = |  |  | 300.1416
Above example assumes sp.gr. = 1.000 | [5 empty] | Above example assumes sp.gr. = 1.000
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 18-2
Example 18-2. Calculate Allowable Silica Concentration in Boiler Feedwater to Prevent Deposition. |  |  |  | Example 18-2. Calculate Allowable Silica Concentration in Boiler Feedwater to Prevent Deposition.
Given: |  |  |  | Given:
Boiler operating pressure | = | 400 | psig | Boiler operating pressure | = | 400 | psig
Silica in boiler feedwater | = | 500 | ppmw | Silica in boiler feedwater | = | 500 | ppmw
Silica in steam at 400 psig | = | 0.07 | ppmw
Solubility of silica at 100 psig | = | 0.01 | ppmw
Solution steps |  |  |  | Solution steps
Using Fig. 18-11, determine concentration of "SILICA IN STEAM - ppmw" (y-axis) at 100 psia (x-axis), 0.010 ppmw. |  |  |  | Requires using Fig. 18-11 to determine intersections of Saturated Steam curve with Boiler Water Silica - PPMW line for your particular application.
Follow the diagonal "Boiler Water Silica 100 ppmw" line to where it intersects with the Saturated Steam curve at 100 psia. Note it is slightly below 0.01 ppmw Silica in Steam (y-axis). Conclusion: 100 ppmw silica in boiler feedwater will not result in silica deposition from steam vapor at 100 psia. |  |  |  | Follow procedure at left to solve for allowable silica in boiler feedwater.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to , reference to or reliance on the information in thes Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to; temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Limits
LIMITS
Example 18-1 assumes 1.000 specific gravity.
Example 18-2 considers only silica solubility. See Fig 18-12 for other limiting components in bioler feedwater.