## Revisions
GPSA Engineering Data Book 14th Edition
REVISION | DATE | REASON(S) FOR REVISION
0 | 2017-04-01 | Initial release

## Nomenclature
GPSA Engineering Data Book 14th Edition
FIG. 10-1
Nomenclature
A | = | area of heat transfer surface, sq ft | NR | = | modified Reynolds number, (in • lb)/(sq ft • s • cp)
Ai | = | inside surface of tube, sq ft | Nt | = | number of tubes
Ab | = | outside bare tube surface, sq ft | ΔP | = | pressure drop, psi
Ax | = | outside extended surface of tube, sq ft | PF | = | fan total pressure, inches of water
At | = | tube inside cross-sectional area, sq in. (see Fig 9-25) | ρa | = | density of air, lb/cu ft
ACFM | = | actual cubic feet per minute | ρw | = | density of water, lb./cu ft
APF | = | total external area/ft of fintube, sq ft/ft | P | = | temperature ratio (see Fig 10-8)
APSF | = | external area of fintube, sq ft/sq ft of bundle face area | PWL | = | sound pressure level
AR | = | area ratio of fintube compared to the exterior area of 1 in. OD bare tube | PWLN | = | PWL for Nf fans
B | = | correction factor, psi (see Fig 10-14) | Q | = | heat transferred, Btu/h
Cp | = | specific heat at average temperature, Btu/(lb • °F) | rd | = | fouling resistance (fouling factor), (hr • ft2 • °F/Btu)
CMTD | = | corrected mean temperature difference, °F | rf | = | fluid film resistance (reciprocal of film coefficient)
dB(A) | = | overall weighted level of sound at a point distant from noise source based on "A" weighting system | rmb | = | metal resistance referred to outside bare surface
D | = | fan diameter, ft | rmx | = | metal resistance referred to outside extended surface
Di | = | inside tube diameter, in. | R | = | distance in feet (see Eq 10-6)
Do | = | outside, tube diameter, in. | R | = | temperature ratio (see Fig 10-8)
DR | = | density ratio, the ratio of actual air density to the density of dry air at 70 °F and 14.7 psia, 0.0749 lb/cu ft (see Fig 10-16) | RPM | = | fan speed, rotations per minute
f | = | friction factor (see Fig 10-15) | S | = | specific gravity (water = 1.0)
F | = | correction factor (see Fig 10-8) | SPL | = | sound pressure level
Fa | = | total face area of bundles, sq ft | t | = | temperature air-side, °F
Fp | = | air pressure drop factor, in. of water per row of tubes | T | = | temperature tube-side, °F
FAPF | = | fan area per fan, ft2/fan | U | = | overall heat transfer coefficient, Btu/(h • ft2 • °F)
FPM | = | fan tip speed, feet per minute | W | = | mass flow, lb/hr
g | = | local acceleration due to gravity, ft/s2 | Y | = | correction factor, psi/ft (see Fig 10-14)
G | = | mass velocity, lb/(sq ft • s) | Δt | = | temperature change, °F
Ga | = | air face mass velocity, lb/(hr • sq ft) of face area | μ | = | viscosity, cp
Gt | = | tube-side mass velocity, lb/(sq ft • s) | μw | = | viscosity at average tube wall temperature, cp
ha | = | air-side film coefficient, Btu/(h • sq ft • °F) | φ | = | viscosity gradient correction
hs | = | shell-side film coefficient based on outside tube area, Btu/(h • sq ft • °F)
ht | = | tube-side film coefficient based on inside tube area, Btu/(h • sq ft • °F) | Subscripts
HP | = | fan horsepower | a | = | air-side
J | = | J factor (see Fig 10-13) | b | = | bare tube surface basis
k | = | thermal conductivity, Btu/[(hr • sq ft • °F)/ft] | s | = | shell-side
L | = | length of tube, ft | t | = | tube-side
LMTD | = | log mean temperature difference, °F | x | = | extended tube surface basis
N | = | number of rows of tubes in direction of flow | 1 | = | inlet
Nf | = | number of fans | 2 | = | outlet
NP | = | number of tube passes

## Example 10-1
GPSA Engineering Data Book 14th Edition
Example 10-1 -- Procedure for determining a rough, preliminary heat transfer surface area, required plot space, and fan power for an air-cooled exchanger |  |  |  | Example 10-1 -- Procedure for determining a rough, preliminary heat transfer surface area, required plot space, and fan power for an air-cooled exchanger
Required data |  |  |  | Operating Conditions | [5 empty] | Heat Release Curve
Fluid | = | Process Cooling Water |  | Fluid | = | Process Cooling Water |  |  |  | Linear
Heat Load, Q | = | 20000000 | Btu/hr | Heat Load, Q | = | 20000000 | Btu/hr |  |  | Non-Linear
Temperature In | = | 300 | °F | Temperature In | = | 300 | °F
Temperature out | = | 150 | °F | Temperature out | = | 150 | °F
Ambient temperature | = | 100 | °F | Ambient temperature | = | 100 | °F
Fouling factor | = | 0.002 | hr-ft2-degF/Btu | Fouling factor | = | 0.002 | hr-ft2-degF/Btu
Heat release curve | = | Linear |  | Heat release curve | = | Linear
Cp air | = | 0.25 | Btu/lb-degF | Cp air | = | 0.25 | Btu/lb-degF
Basic Assumptions |  |  |  | Air Cooler Design
Type | = | Forced draft, 2 fans |  | Type | = | 2 | Fans, forced draft
Fintube | = | 1 in OD, 5/8 in high fins |  | OD (fintube) | = | 1 | in.
Tube pitch | = | 2-3/8 in triangular |  | Fin height | = | 0.625 | in. high fins
Bundle layout | = | 4 tube passes, 6 rows of tubes |  | Tube pitch | = | 2.375 | in. triangular (Δ)
|  |  |  | Np | = | 4 | tube passes
First Trial |  |  |  | N | = | 6 | tube rows
1. Pick an appropriate overall heat transfer coefficient, Ux | = | 5.2 | Btu/hr-ft2-degF (see Fig 10-10, for Process Water and 5/8 inch by 10) | Air Cooler Thermal Parameters
2. Determine the appropriate external area of fintube per sq.sf. of bundle area, APSF | = | 169.6 | ft2/ft2 (see Fig 10-11, for 6 rows, 5/8 high fins, 2-3/8 triangular tube pitch) | Ux | = | 5.2 | Btu/hr-ft2-degF |  | Fig 10-10
3. Determine the LMTD correction factor | = | 1 | Dimensionless. Use 1.0 for 3 or more tube passes, otherwise use Figs. 10-8 or 10-9. | APSF | = | 169.6 | ft2/ft2 |  | Fig 10-11
4. Assume t2 and calculate the CMTD, with countercurrent temperature profile. | = | 200 | degF | LMTD correction factor | = | 1 | Dimensionless.
Calculate CMTD = (F)(LMTD) | = | 72.1348 | degF | t2, assumed | = | 200 | degF |  | Change until it agrees with t2, actual.
5. Calculate Ax | = | 53319.0139 | sq. ft. | t2, Actual
6. Based on APSF, calculate the air-side face area, Aa | = | 314.381 | sq. ft. | CMTD | = | 72.1348 | degF
7. Calculate the air-side mass flow rate (Wa, lb/hr) using Aa and based on a typical face velocity of 600 Std. ft/min. | = | 848828.6409 | lb/hr | Ax | = | 53319.0139 | sq. ft.
8. Check actual t2 from exchanger (t2,actual) | = | 194.2475 | °F | Aa | = | 314.381 | sq. ft.
9. Repeat steps 4 through 8 by iterating t2 until convergence is achieved | = | 196.2 | °F | Wa | = | 848828.6409 | lb/hr
Recalculation of Step 4, CMTD | = | 73.6539 | °F | t2,actual | = | 194.2475 | °F
Recalculation of Step 5, Ax | = | 52219.2569 | sq. ft.
Recalculation of Step 6, Aa | = | 307.8966 | sq. ft. | Air Cooler Dimensions
Recalculation of Step 7, Wa | = | 831320.7169 | sq. ft. | Bay width | = | 10.2369 | ft | Bay width does not exceed 15 feet
Recalculation of Step 8, t2,actual | = | 196.2324 | °F | Bay length | = | 30.7106 | ft | Bay length does not exceed 45 feet
The recalculated Step 6, face area (Aa), shows a bay size of 10 ft X 30 ft (300 sq.ft) will be adequate.
Bay width | = | 10 | ft | Fan Horsepower
Bay length | = | 30 | ft | Fan horsepower | = | 18.63 | bhp per fan
Calculate fan horsepower by extrapolating from two 40 BHP fans on a 15 ft X 45 ft unit. | = | 17.7778 | bhp per fan (two required)
Length to width ratio is typically 3:1
Truck shippable units do not exceed 15 ft X 45 ft
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 10-2
GPSA Engineering Data Book 14th Edition
Example 10-2 Part 1 -- Procedure for estimating transfer surface, plot area, and horsepower | [6 empty] | Example 10-2 Parts 1 & 2 -- Procedure for estimating transfer surface, plot area, and horsepower
Given Data: | [6 empty] | Given Data:
Required Data For Hot Fluid | [6 empty] | Required Data For Hot Fluid
Name and Phase | = | 48°API | hydrocarbon liquid |  |  |  | API | = | 48 | °API
Physical Props at avg temp | = | 200 | °F |  |  |  | Phase | = | hydrocarbon liquid
Specific Heat Cp | = | 0.55 | Btu/(lb • °F) |  |  |  | Avereage Temperature | = | 200 | °F
Viscosity μ | = | 0.51 | cp |  |  |  | Cp | = | 0.55 | Btu/(lb • °F)
Thermal Conductivity k | = | 0.0766 | Btu/[(hr • sq ft • °F)/ft] |  |  |  | μ | = | 0.51 | cp
Heat Load Q | = | 15000000 | Btu/hr |  |  |  | k | = | 0.0766 | Btu/[(hr • sq ft • °F)/ft]
Flow Quantity Wt | = | 273000 | lb/hr |  |  |  | Q | = | 15000000 | Btu/hr
Temperature In T1 | = | 250 | °F |  |  |  | Wt | = | 273000 | lb/hr
Temperature Out T2 | = | 150 | °F |  |  |  | T1 | = | 250 | °F
Fouling Factor rdt | = | 0.001 | (hr • sq ft • °F)/Btu |  |  |  | T2 | = | 150 | °F
Allowable Press Drop ΔPt | = | 5 | psi |  |  |  | rdt | = | 0.001 | (hr • sq ft • °F)/Btu
Required Data For Air | [6 empty] | ΔPt (allowable) | = | 5 | psi
Ambient Temperature t1 | = | 100 | °F |  |  |  | Required Data For Air
Elevation | = | Sea level | See Fig 10-16 for Altitude Correction |  |  |  | t1 | = | 100 | °F
CPair | = | 0.24 | Btu/(lb • °F) |  |  |  | Elevation | = | Sea level | See Fig 10-16 for Altitude Correction
Air density, 70 degF, sea level | = | 0.0749 | lb/cu.ft |  |  |  | CPair | = | 0.24 | Btu/(lb • °F)
Density Ratio Air DR, air | = | 0.94 | dimensionless |  |  |  | Air density, 70 degF, sea level | = | 0.0749 | lb/cu.ft
Basic Assumptions | [6 empty] | DR, air | = | 0.94 | dimensionless
Type | = | 2 | Fans, Forced Draft |  |  |  | Basic Assumptions
Fintube Do | = | 1 | in. OD |  |  |  | Type | = | 2 | Fans, Forced Draft
|  | 0.625 | in. high fins |  |  |  | Fan Efficiency | = | 70%
Tube pitch | = | 2.5 | in. triangular (Δ) |  |  |  | Fan Motor Speed Reducer Efficiency | = | 92%
Bundle Layout NP | = | 3 | tube passes |  |  |  | Fintube
N | = | 4 | rows of tubes |  |  |  | Do | = | 1 | in. OD
L | = | 30 | ft long tubes |  |  |  | Fin Height |  | 0.625 | in.
Data Collected From Figures in Text | [6 empty] | Tube pitch | = | 2.5 | in. triangular (Δ)
APSF | = | 107.2 | sq.ft./sq.ft. |  |  | Fig 10-11 | Bundle Layout
APF | = | 5.58 | sq ft/ft |  |  | Fig 10-11 | NP | = | 3 | tube passes
At | = | 0.5945 | in2 |  |  | Fig 9-25 | N | = | 4 | rows of tubes
Di | = | 0.87 | in. |  |  | Fig 9-25 | L | = | 30 | ft long tubes
φ | = | 0.96 | dimensionless |  |  | Fig 10-19 | Data Collected From Figures in Text
k • [(Cp • μ)/k]1/3 | = | 0.12 | sq.ft./sq.ft. |  |  | Fig 10-12 | APSF | = | 107.2 | sq.ft./sq.ft. | Fig 10-11
AR | = | 21.4 | sq ft/sq ft |  |  | Fig 10-11 | APF | = | 5.58 | sq ft/ft | Fig 10-11
[7 empty] | At | = | 0.5945 | in2 | Fig 9-25
To determine Approximate Air Temperature Rise | [6 empty] | Di | = | 0.87 | in. | Fig 9-25
[7 empty] | φ | = | 0.96 | dimensionless | Fig 10-19
Δta | = | [(Ux+1)/10] • [((T1+T2)/2)-t1] |  |  |  |  | k • [(Cp • μ)/k]1/3 | = | 0.12 | sq.ft./sq.ft. | Fig 10-12
|  | See Intermediate Calculations below. |  |  |  |  | AR | = | 21.4 | sq ft/sq ft | Fig 10-11
To determine t2 | [6 empty] | Data to be collected subsequent to with Surface Area calculations
[7 empty] | Y | = | 14.5 | psi/ft | Fig 10-14
t2 | = | t1 + Δta |  |  |  |  | B | = | 0.25 | psi/tube pass | Fig 10-14
[7 empty] | f | = | 0.0024 |  | Fig 10-15
To determine LMTD | [6 empty] | J | = | 1900 |  | Fig 10-13
[7 empty] | ha | = | 8.5 | Btu/(hr-degF-ft2) | Fig 10-17
LMTD | = | (GTTD-LTTD)/ln(GTTD/LTTD) |  |  |  | Fig 9-3 | Fp | = | 0.1 | in. H2O/row of tubes | Fig 10-18
[7 empty] | DR | = | 0.94 |  | Fig 10-16
To determine CMTD
Air Cooler Thermal Parameters
CMTD | = | LMTD • F1 |  |  |  |  | Ux | = | 4.2 | Btu/(h • ft2 • °F)
[7 empty] | F1 | = | 1 | Dimensionless | Fig 9-4
To determine Outside Extended Surface of Tube | [6 empty] | Corrected Mean Temperature Difference
[7 empty] | Δta | = | 52 | °F
Ax | = | Q/(Ux • CMTD) |  |  |  |  | t2 | = | 152 | °F
[7 empty] | Hot side Δt | = | 98
To determine Total Face Area of Bundles | [6 empty] | Cold side Δt | = | 50
[7 empty] | GTTD | = | 98 | °F
Fa | = | Ax/APSF |  |  |  |  | LTTD | = | 50 | °F
[7 empty] | LMTD | = | 71.3283 | °F
To determine the Unit Width | [6 empty] | CMTD | = | 71.3283 | °F
Width | = | Fa/L |  |  |  |  | Surface Area
[7 empty] | Ax | = | 50070.2733 | ft2
To determine the Number of Tubes | [6 empty] | Fa | = | 465 | ft2
[7 empty] | Width | = | 15.5 | ft
Nt | = | Ax/(APF • L) |  |  |  |  | Tube Suface Area | = | 465 | ft2
[7 empty] | Extended Tube Surface Area | = | 49848 | ft2
To determine the Tubeside Mass Velocity
Tubeside Pressure Drop
Gt | = | (144 • Wt • Np)/(3600 • Nt • At) |  |  |  |  | Nt | = | 299.1056
[7 empty] | Gt | = | 184.233 | lb/(ft2 • sec)
To determine the Modified Reynolds Number | [6 empty] | NR | = | 314.2799
[7 empty] | Specific Gravity | = | 0.7883
NR | = | (Di • Gt)/μ |  |  |  |  | ΔPt | = | 4.0125 | psi | Calculated ΔP < Allowable ΔP
To determine the Tube-Side Pressure Drop | [6 empty] | Heat Transfer
[7 empty] | ht | = | 251.5862
ΔPt | = | [(f • Y • L • Np)/φ] + (B • Np) |  |  |  | Fig 10-14, 10-15 | Wa | = | 1201923.0769 | lb/hr
[7 empty] | Ga | = | 2584.7808 | lb/hr-sq.ft. face area
Intermediate Calculations (not shown) | [6 empty] | Ax/Ai | = | 24.5977
[7 empty] | 1/Ux | = | 0.24002
1. Pick Approximate Overall Transfer Coefficient from Fig 10-10 | [6 empty] | Ux | = | 4.1664 | Btu/(h • ft2 • °F)
Ux |  |  |  | = | 4.2 | Btu/(h • ft2 • °F)
If Ux calculated is equal or slightly greater than Ux assumed at beginning and calculated pressure drop is within allowable pressure drop, the solution is acceptable. Otherwise repeat steps 1-15 assuming a new Ux between original assumed value and calculated value
2. Calculate Approximate Air Temperature Rise | [6 empty] | solution is acceptable. Otherwise repeat steps assuming a new Ux between original assumed value and calculated value.
Δta | = | [(4.2+1)/10] • [((250+150)/2)-100] |  | = | 52 | °F
Fan Calculations
t2 | = | 100 + 52 |  | = | 152 | °F | FAPF | = | 93 | ft2
[7 empty] | D | = | 11 | ft
3. Calculate CMTD |  | hot side | cold side |  |  |  | Ta, avg | = | 126 | °F
Hydrocarbon |  | 250 | 150 |  |  |  | ΔPa | = | 0.42553 | in. H2O
Air |  | 152 | 100 |  |  |  | Actual Air Volume | = | 284521.934 | ACFM Total
|  | 98 | 50 |  |  |  |  | = | 142260.967 | ACFM per Fan
[7 empty] | PF | = | 0.55686 | in. H2O
GTTD |  |  |  | = | 98 | °F | bhp per fan | = | 17.8052 | hp
LTTD |  |  |  | = | 50 | °F | Fan Motor hp | = | 19.3535 | hp
[8 empty] | = | 20 | hp
LMTD | = | (98-50)/[ln(98/50)] |  | = | 71.3283 | °F
Alternatively, use Fig. 9-3 LMTD diagram
Use Fig 9-4 to Find F1
F1 |  |  |  | = | 1
CMTD | = | 71.3 • 1.0 |  | = | 71.3283 | °F
4. Calculate AX
Ax | = | 15000000/(4.2 • 53.5) |  | = | 50070.2733 | ft2
5. Calculate Face Area Using APSF factor from Fig 10-11
Fa | = | 50,700/107.2 |  | = | 465 | ft2
6. Calculate Unit Width with Assumed Tube Length
Width | = | 465/30 |  | = | 15.5 | ft
7. Calculate the Number of Tubes Using APF factor from Fig 10-11
Nt | = | 50,070/(5.58 • 30) |  | = | 299.1056
8. Calculate Tube-Side Mass Velocity from Assumed number of passes and reading At from Fig 9-25 for a 1 in. OD x 16 BWG tube
Gt | = | (144 • 273000 • 3)/(3600 • 299 • 0.5945) |  | = | 184.233 | lb/(ft2 • sec)
9. Calculate Modified Reynolds number
NR | = | (0.87 • 184)/0.51 |  | = | 314.2799
10. Calculate Tube-Side Pressure Drop using Equation from Fig 10-14 and Fig 10-15
Use Fig 10-14 to find Y and B
Y |  |  |  | = | 14.5 | psi/ft
B |  |  |  | = | 0.25 | psi/tube pass
Use Fig 10-15 to find f using NR
f |  |  |  | = | 0.0024
ΔPt | = | [(0.0024 • 14.5 • 30 • 3)/0.96] + (0.25 • 3) |  | = | 4.0125 | psi
Example 10-2 Part 2 -- Procedure for estimating transfer surface, plot area, and horsepower
To determine the Tube-Side Film Coefficient
ht | = | [J • (k • ((Cp • μ)/k)1/3) • φ]/Di |  |  |  | Fig 10-13
See Intermediate Calculations below.
To determine Air Quality
Wa | = | Q/(0.24 • Δta)
To determine Air Face Mass Velocity
Ga | = | Wa/Fa
To determine Ax/Ai
Ax/Ai | = | (AR • Do)/Di
To determine Overall Transfer Coefficient
1/Ux | = | [(1/ht) • (Ax/Ai)] + [(rdt • (Ax/Ai)] + rmx + (1/ha)
To determine Minimum Fan Area Per Fan
FAPF | = | (0.4 • Fa)/Nf
To determine Fan Diameter
D | = | [(4 • FAPF)/π]0.5
To determine Air Static Pressure Drop
ΔPa | = | (Fp • N)/DR
To determine Actual Air Volume
ACFM | = | Wa/(DR • 60 • DR, air)
To determine the fan Total Pressure
PF | = | ΔPa + [ACFM/(4005 • ((π • D2)/4))]2 • DR
To determine the Brake Horsepower Per Fan
bhp | = | [(ACFM/fan) • PF]/(6356 • 0.7)
Intermediate Calculations (not shown)
11. Calculate Tube-Side Film Coefficient using Equation from Fig 10-13
Using Fig 10-13 to find J Factor using NR = 314 from Part 1.
J |  |  |  | = | 1900
ht | = | (1900 • 0.12 • 0.96)/0.87 |  | = | 251.5862
12. Calculate Air Quantity
Wa | = | 15000000/(0.24 • 52) |  | = | 1201923.0769 | lb/hr
13. Calculate Air Face Mass Velocity
Ga | = | 1201923/465 |  | = | 2584.7808 | lb/hr-sq.ft. face area
14. Read Air-Side Film Coefficient from Fig 10-17
ha |  |  |  | = | 8.5 | Btu/(hr-degF-ft2)
15. Calculate Overall Transfer Coefficient
Ax/Ai | = | (21.4 • 1.0)/0.87 |  | = | 24.5977
1/Ux | = | [(1/252) • 24.6] + (0.001 • 24.6) + (1/8.5) |  | = | 0.24002
Note: rmx is ommitted since metal resistance is small compared to other resistances
Ux | = | 1/0.240 |  | = | 4.1664 | Btu/(h • ft2 • °F)
If Ux calculated is equal or slightly greater than Ux assumed at beginning and calculated pressure drop is within allowable pressure drop then the solution is acceptable. Otherwise repeat steps 1-15 assuming a new Ux between original assumed value and calculated value
16. Calculate Minimum Fan Area
FAPF | = | (0.4 • 465)/2 |  | = | 93 | ft2
17. Calculate Fan Diameter
D | = | [(4 • 93)/π]0.5 |  | = | 11 | ft
18. Calculate Air Static Pressure Drop
Ta, avg | = | (100+152)/2 |  | = | 126 | °F
Use Fig 10-18 to find Fp using Ga
Fp |  |  |  | = | 0.1 | in. H2O/row of tubes
Use Fig 10-16 to find DR using Ta, avg
DR |  |  |  | = | 0.94
ΔPa | = | (0.1 • 4)/0.94 |  | = | 0.42553 | in. H2O
19. Calculate Actual Air Volume using DR of Air at Fan Inlet
ACFM | = | 1201923/(0.94 • 60 • 0.0749) |  | = | 284521.934 | Total
|  |  |  | = | 142260.967 | per Fan
20. Approximate Fan Total Pressure using DR of Air at Fan and Fan Area
PF | = | 0.43 + [142261/(4005 • ((π • 112)/4))]2 • 0.94 |  | = | 0.55686 | in. H2O
21. Approximate Brake Horsepower Per Fan, using 70% Fan Efficiency
Fan Efficiency |  |  |  | = | 0.7
bhp | = | (142261 • 0.56)/(6356 • 0.7) |  | = | 17.8052
Actual Fan Motor needed for 92% Efficient Speed reducer
|  |  |  | = | 0.92
bhp | = | 17.81/0.92 |  | = | 19.3535 | hp
|  |  |  | = | 20 | hp
Calculate Extended Surface Area
A | = | 15.5 • 30 |  | = | 465 | ft2
A | = | 465 • 107.2 |  | = | 49848 | ft2
One Unit having
| 49848 | ft2 of extended area
| 11 | ft diameter fans
| 20 | hp fan drivers
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Limits
GPSA Engineering Data Book 14th Edition
LIMITS
Limit air out temp to 200 degF. Prevent damaging fan blades, bearings, V-belts.
Use forced air fan for process fluids above 350 degF. Prevent fan blade and bearing failure.
Angle condensing surfaces to allow positive drainage.
Fan size ranges from 3 to 28 ft. diameter.
Limit fan tip air speed to 12,000 fpm.
Use V-belt drives up to about 30 bhp. Gear drives above 30 bhp.
Limit driver size to 50 bhp.
Use tension wrapped finned tubes for service below 400 deg F process fluid.
Air face velocity is typically 600 SCF/min.
For warm air recirculation, keep air flow below 500 ft/min.
Truck shippable air coolers do not exceed typically 15 ft X 45 ft
Avoid placing bank of coolers downwind from other heat gererating equipment.
Normally, the bank should be oriented such that the wind flows parallel to the long axis of the bank of coolers.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processor Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.