## Revisions
GPSA Engineering Data Book 14th Edition
REVISION | DATE | REASON(S) FOR REVISION
0 | 2017-04-01 | Initial release

## Nomenclature
GPSA Engineering Data Book 14th Edition
FIG. 17-1
Nomenclature
A | = | pipe cross sectional area, ft2 (A=πD2/4) | ΔP100 | = | pressure drop, psi/100 ft equivalent pipe length
c | = | sum of allowances for corrosion, erosion, etc., in., Fig 17-22 | ΔPe | = | elevation component of pressure drop, psi
C | = | design parameter used in Hazen and Williams formula, Eq 17-33 | ΔPf | = | frictional component of pressure drop, psi
C1 | = | discharge factor from Fig 17-8 | ΔPt | = | total pressure drop, psi
C2 | = | size factor from Fig 17-9 | ΔPwh | = | pressure increase due to water hammer, psi
d | = | internal diameter of pipe, in. | q | = | flow rate, gal/min
do | = | outside pipe diameter, in. | Q | = | flow rate of gas, cubic feet per day at base conditions
D | = | internal diameter of pipe, feet | QL | = | liquid volumetric flow rate at flowing conditions, ft3/sec
E | = | pipeline efficiency factor (fraction) | Qg | = | gas volumetric flow rate at flowing conditions, ft3/sec
E' | = | longitudinal weld joint factor from ANSI B31.3, Fig 17-22 | Re | = | Reynolds number
E" | = | longitudinal joint factor from ANSI B31.8, Fig 17-23 | Rey | = | mixture Reynolds number for Dukler calculation, from Eq 17-46
ff | = | Fanning friction factor | S | = | specific gravity of flowing gas (air = 1.0)
fm | = | Moody friction factor (fm = 4.0 ff) | S' | = | allowable stress, psi, Fig 17-22
fn | = | single phase friction factor for Dukler calculation, from Eq 17-45 | S" | = | specified minimum yield strength, psi, Fig 17-23
ftpr | = | friction factor ratio for Dukler calculation, Fig 17-17 | t | = | thickness, in., Figs 17-22, 17-23
F" | = | construction type design factor used in ANSI B31.8, Fig 17-24 | tm | = | minimum required wall thickness, in., Fig 17-22
Fpv | = | volume correction for a non-ideal fluid due to compressibility from Eq 17-13 | T | = | absolute temperature of flowing gas, °R
(1/ff)1/2 | = | transmission factor | T" | = | temperature derating factor used in ANSI B31.8, Fig 17-23
g | = | acceleration due to gravity, 32.2 ft/sec2 | Tavg | = | average temperature, °R [Tavg=1/2(Tin+Tout)]
gc | = | gravitational constant, 32.2 (ft • lbm)/(lbf • sec2) | Tb | = | base absolute temperature, °R (ANSI 2530 specification: Tb= 520 °R)
hL | = | loss of static pressure head due to fluid flow, feet of fluid | V | = | single phase fluid velocity, ft/sec
H | = | total energy of a fluid at a point above a datum, from Eq 17-1 | Va | = | acoustic velocity of fluid, ft/sec
HLd | = | liquid holdup fraction (Dukler), Fig 17-18 | Vsg | = | superficial gas velocity, ft/sec, from Eq 17-37
HLe | = | liquid holdup faction (Eaton), Fig 17-20 | VsL | = | superficial liquid velocity, ft/sec, from Eq 17-36
HLf | = | liquid holdup fraction (Flanigan), Fig 17-19 | Vm | = | mixture velocity, ft/sec, from Eq 17-47
IL | = | liquid inventory in pipe, ft3, from Eq 17-58 | W | = | mass flow, lb/hr
L | = | length of line, feet | XA | = | Aziz fluid property correction factor (horizontal axis, Fig 17-16)
Lm | = | length of line, miles | YA | = | Aziz fluid property correction factor (vertical axis, Fig 17-16)
MW | = | molecular weight | Y' | = | coefficient found in Table 304.1.1, ANSI B31.3, Fig 17-22
Nx | = | Fig 17-16 horizontal coordinate, ft/sec | Zavg | = | average compressibility factor
Ny | = | Fig 17-16 vertical coordinate, ft/sec | Ze | = | pipeline vertical elevation rise, ft
NE | = | abscissa of Eaton correlation, Fig 17-20 | Greek
NLv | = | liquid velocity number, from Eq 17-54 | ε | = | absolute roughness, ft
Ngv | = | gas velocity number, from Eq 17-55 | λ | = | flowing liquid volume fraction
Nd | = | pipe diameter number, from Eq 17-56 | μe | = | single phase fluid viscosity, lbm/(ft • sec)
NL | = | liquid viscosity number, from Eq 17-57 | μ | = | single phase fluid viscosity, cp
P | = | pressure, psia | μg | = | gas viscosity, cp
P1 | = | inlet pressure, psia | μL | = | liquid viscosity, cp
P2 | = | outlet pressure, psia | μn | = | mixture viscosity for Dukler calculation, cp
Pavg | = | average pressure, psia, from Eq 17-16 | ρ | = | single phase fluid density, lb/ft3
Pb | = | base absolute pressure, psia (ANSI 2530 specification: Pb = 14.73 psia) | ρavg | = | average density, lb/ft3 [ρavg=1/2(ρin+ρout)]
Pi | = | internal design pressure, psig | ρa | = | air density at 60 °F and 14.7 psia, 0.0764 lb/ft3
|  |  | ρw | = | water density at 60 °F and 14.7 psia, 62.4 lb/ft3
|  |  | ρg | = | gas density, lb/ft3
|  |  | ρL | = | liquid density, lb/ft3
|  |  | ρk | = | two phase mixture density for Dukler calculation, lb/ft3
|  |  | σ | = | interfacial tension at flowing conditions, dyne/cm
|  |  | σwa | = | interfacial tension of air and water at 60 °F and 14.7 psia, 72.4 dyne/cm

## Example 17-1
GPSA Engineering Data Book 14th Edition
Example 17-1 -- Calculate the pressure drop in a 10-in., Schedule 40 pipe for a flow of 150,000 lb/hr of methane (MW=16.043). Temperature is 60 °F and pressure is 750 psia. The compressibility factor is 0.905 (from Fig 23-5). |  |  |  |  | Example 17-1 -- Calculate the pressure drop in a 10-in., Schedule 40 pipe for a flow of 150,000 lb/hr of methane (MW=16.043). Temperature is 60 °F and pressure is 750 psia. The compressibility factor is 0.905 (from Fig 23-5).
Given: |  |  |  |  | Given:
Temperature | = | 60 | °F |  | Temperature | = | 60 | °F
Pressure | = | 750 | psia |  | Pressure | = | 750 | psia
Flowrate | = | 150000 | lb/hr |  | Flowrate | = | 150000 | lb/hr
Compressibility Factor Z | = | 0.905 |  |  | Compressibility Factor Z | = | 0.905
Molecular Weight | = | 16.043 |  |  | Molecular Weight | = | 16.043
Nominal Pipe Size | = | 10 | inch |  | Nominal Pipe Size | = | 10 | inch
Schedule Number | = | 40 |  |  | Schedule Number | = | 40
Gas Constant | = | 10.73 | psia ft3/lbmol °R |  | Gas Constant | = | 10.73 | psia ft3/lbmol °R
Calculations: |  |  |  |  | Calculations:
ρ | = | (16.043*750)/(10.73*520*0.905)=2.38 | lb/ft3 |  | ρ | = | 2.3828 | lb/ft3
C1 | = | 22.5 | (using Fig. 17-8) |  | C1 | = | 22.5 |  | (using Fig. 17-8)
C2 | = | 0.0447 | (using Fig. 17-9) |  | C2 | = | 0.0447 |  | (using Fig. 17-9)
ΔP100 | = | (22.5*0.0447)/2.38=0.422 | psi/100 ft | (from Eq. 17-31) | ΔP100 | = | 0.42208 | psi/100 ft | (from Eq. 17-31)
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processors Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 17-2
GPSA Engineering Data Book 14th Edition
Example 17-2 -- Calculate the required line size (of Schedule 40 pipe) to give ΔP100 = 1 psi or less when flowing 75,000 lb/hr of methane (MW=16.043) at 400 psia and 100 °F. The compressibility factor is 0.96 (from Fig 23-5). |  |  |  |  | Example 17-2 -- Calculate the required line size (of Schedule 40 pipe) to give ΔP100 = 1 psi or less when flowing 75,000 lb/hr of methane (MW=16.043) at 400 psia and 100 °F. The compressibility factor is 0.96 (from Fig 23-5).
Given: |  |  |  |  | Given:
Temperature | = | 100 | °F |  | Temperature | = | 100 | °F
Pressure | = | 400 | psia |  | Pressure | = | 400 | psia
Mass Flowrate | = | 75000 | lb/hr |  | Mass Flowrate | = | 75000 | lb/hr
Molecular Weight | = | 16.043 |  |  | Molecular Weight | = | 16.043
Compressibility Factor Z | = | 0.96 |  |  | Compressibility Factor Z | = | 0.96
Pipe Schedule Number | = | 40 |  |  | Pipe Schedule Number | = | 40
Max. ΔP100 | <= | 1 | psi/100 ft |  | Max. ΔP100 | <= | 1 | psi/100 ft
Gas Constant | = | 10.73 | psia ft3/lbmol °R |  | Gas Constant | = | 10.73 | psia ft3/lbmol °R
Calculations: |  |  |  |  | Calculations:
ρ | = | (16.043*400)/(10.73*560*0.96)=1.11 | lb/ft3 |  | ρ | = | 1.1125 | lb/ft3
C1 | = | 5.6 |  | (from Fig. 17-8) | C1 | = | 5.6 |  | (from Fig. 17-8)
Minimum C2 value | = | (1*1.11)/5.6=0.20 |  |  | Minimum C2 value | = | 0.19865
Actual C2 value | = | 0.146 |  | (from Fig. 17-9) | Actual C2 value | = | 0.146 |  | (from Fig. 17-9)
Nominal pipe size | = | 8 | inch |  | Nominal pipe size | = | 8 | inch
Actual ΔP100 | = | (5.6*0.146)/1.11=0.73 | psi/100 ft |  | Actual ΔP100 | = | 0.73494 | psi/100 ft
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processors Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 17-3
GPSA Engineering Data Book 14th Edition
Example 17-3 -- A vapor-liquid mixture is flowing vertically upward in a pipe having an inside diameter of 8.0 inches. The fluid is a hydrocarbon liquid-hydrocarbon vapor mixture. The liquid density is 52 lb/ft3 and the vapor density is 2.0 lb/ft3. The interfacial surface tension is 20 dynes/cm. The liquid volumetric flow rate is 0.17 ft3/sec and the vapor flow rate is 0.5 ft3/sec measured at actual conditions. What flow regime is to be expected? |  |  |  | Example 17-3 -- A vapor-liquid mixture is flowing vertically upward in a pipe having an inside diameter of 8.0 inches. The fluid is a hydrocarbon liquid-hydrocarbon vapor mixture. The liquid density is 52 lb/ft3 and the vapor density is 2.0 lb/ft3. The interfacial surface tension is 20 dynes/cm. The liquid volumetric flow rate is 0.17 ft3/sec and the vapor flow rate is 0.5 ft3/sec measured at actual conditions. What flow regime is to be expected?
Given: |  |  |  | Given:
ρL | = | 52 | lb/ft3 | ρL | = | 52 | lb/ft3
ρg | = | 2 | lb/ft3 | ρg | = | 2 | lb/ft3
ρw | = | 62.4 | lb/ft3 | ρw | = | 62.4 | lb/ft3
ρa | = | 0.0764 | lb/ft3 | ρa | = | 0.0764 | lb/ft3
σ | = | 20 | dynes/cm | σ | = | 20 | dynes/cm
σwa | = | 72.4 | dynes/cm | σwa | = | 72.4 | dynes/cm
QL | = | 0.17 | ft3/sec | QL | = | 0.17 | ft3/sec
Qg | = | 0.5 | ft3/sec | Qg | = | 0.5 | ft3/sec
D | = | 8 | in | D | = | 8 | in
Solution: |  |  |  | Solution:
YA | = | [(52*72.4)/(62.4*20)]0.25=1.32 |  | YA | = | 1.3179
XA | = | [(2/0.0764)0.333] •1.32=3.91 |  | XA | = | 3.9089
A | = | (π*(0.667)2)/4=0.35 | ft2 | A | = | 0.34907 | ft2
Vsg | = | 0.5/0.35=1.43 | ft/sec | Vsg | = | 1.4324 | ft/sec
VsL | = | 0.17/0.35=0.49 | ft/sec | VsL | = | 0.48701 | ft/sec
Nx | = | 1.43*3.91=5.60 | ft/sec | Nx | = | 5.5991 | ft/sec
Ny | = | 0.49*1.32=0.64 | ft/sec | Ny | = | 0.64183 | ft/sec
Use Fig 17-16 and Nx, Ny to determine what flow regime should be expected |  |  |  | Use Fig 17-16 and Nx, Ny to determine what flow regime should be expected
(Nx, Ny) | = | (5.60, 0.64) |  | (Nx, Ny) | = | (5.60, 0.64)
Flow regime | = | Slug |  | Flow regime | = | Slug
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processors Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Example 17-4
GPSA Engineering Data Book 14th Edition
Example 17-4 -- A pipeline segment with a 6-inch inside diameter, 0.75 miles long, transports a mixture of gas and oil. The pipeline has a gradual upward slope and rises 100 feet over the 0.75 mile length. The inlet pressure of the pipeline is 400 psia, liquid viscosity is 20 cp, the vapor viscosity is 0.015 cp, and the interfacial surface tension is 15 dynes/cm. The liquid flow rate is 10 ft3/min and the vapor flow rate is 250 actual ft3/min. The density of the liquid phase is 55 lb/ft3, and the density of the gas phase is 1.3 lb/ft3 at operating conditions. What is the pressure at the downstream end of the line segment, and what is the liquid inventory of the line? |  |  |  |  | Example 17-4 -- A pipeline segment with a 6-inch inside diameter, 0.75 miles long, transports a mixture of gas and oil. The pipeline has a gradual upward slope and rises 100 feet over the 0.75 mile length. The inlet pressure of the pipeline is 400 psia, liquid viscosity is 20 cp, the vapor viscosity is 0.015 cp, and the interfacial surface tension is 15 dynes/cm. The liquid flow rate is 10 ft3/min and the vapor flow rate is 250 actual ft3/min. The density of the liquid phase is 55 lb/ft3, and the density of the gas phase is 1.3 lb/ft3 at operating conditions. What is the pressure at the downstream end of the line segment, and what is the liquid inventory of the line?
Given: |  |  |  |  | Given:
D | = | 6 | in |  | D | = | 6 | in
Lm | = | 0.75 | miles |  | Lm | = | 0.75 | miles
DZe | = | 100 | feet |  | DZe | = | 100 | feet
P1 | = | 400 | psia |  | P1 | = | 400 | psia
μL | = | 20 | cp |  | μL | = | 20 | cp
μg | = | 0.015 | cp |  | μg | = | 0.015 | cp
σ | = | 15 | dynes/cm |  | σ | = | 15 | dynes/cm
QL | = | 10 | ft3/min |  | QL | = | 10 | ft3/min
Qg | = | 250 | actual ft3/min |  | Qg | = | 250 | actual ft3/min
ρL | = | 55 | lb/ft3 |  | ρL | = | 55 | lb/ft3
ρg | = | 1.3 | lb/ft3 |  | ρg | = | 1.3 | lb/ft3
Pb | = | 14.73 | psia |  | Pb | = | 14.73 | psia
Solution: |  |  |  |  | Solution:
λ | = | 10/(250 + 10)=0.038 |  | (from Eq.17-44) | λ | = | 0.038462 |  | (from Eq.17-44)
μn | = | (20*0.038) + (0.015*(1-0.038))=0.784 | cp | (from Eq.17-48) | μn | = | 0.78365 | cp | (from Eq.17-48)
Assumed HLd | = | 0.038 |  |  | Assumed HLd | = | 0.038462
ρk | = | [(55*0.0382)/0.038] + [(1.3*(1-0.038)2)/(1-0.038)]=3.37 | lb/ft3 | (from Eq.17-43) | ρk | = | 3.3654 | lb/ft3 | (from Eq.17-43)
A | = | (π*(6/12)2)/4=0.196 | ft2 |  | A | = | 0.19635 | ft2
VsL | = | 0.1667/0.196=0.85 | ft/sec | (from Eq.17-36) | VsL | = | 0.84883 | ft/sec | (from Eq.17-36)
Vsg | = | 4.1667/0.196=21.22 | ft/sec | (from Eq.17-37) | Vsg | = | 21.2207 | ft/sec | (from Eq.17-37)
Vm | = | 0.849 + 21.22=22.07 | ft/sec | (from Eq.17-47) | Vm | = | 22.0695 | ft/sec | (from Eq.17-47)
Mixture Rey | = | (124*3.365*22.07*6)/0.784=70514 |  | (from Eq.17-46) | Mixture Rey | = | 70514.0369 |  | (from Eq.17-46)
Trial HLd | = | 0.12 |  | (from Fig 17-18) | Trial HLd | = | 0.12 |  | (from Fig 17-18)
ρk | = | [(55*0.0382)/0.12] + [(1.3*(1-0.038)2)/(1-0.12)]=2.04 | lb/ft3 | (from Eq.17-43) | ρk | = | 2.0438 | lb/ft3 | (from Eq.17-43)
Rey | = | (124*2.044*22.07*6)/0.784=42824 |  | (from Eq.17-46) | Rey | = | 42823.8344 |  | (from Eq.17-46)
Trial HLd |  | 0.16 |  | (from Fig 17-18) | Trial HLd |  | 0.16 |  | (from Fig 17-18)
ρk | = | [(55*0.0382)/0.16] + [(1.3*(1-0.038)2)/(1-0.16)]=1.94 | lb/ft3 | (from Eq.17-43) | ρk | = | 1.9394 | lb/ft3 | (from Eq.17-43)
Rey | = | (124*1.939*22.07*6)/0.784=40635 |  | (from Eq.17-46) | Rey | = | 40635.0514 |  | (from Eq.17-46)
Final HLd |  | 0.16 |  | (from Fig 17-18) | Final HLd |  | 0.16 |  | (from Fig 17-18)
fn | = | 0.0056 + 0.5*(40635)-0.32=0.022 |  | (from Eq.17-45) | fn | = | 0.022354 |  | (from Eq.17-45)
ftpr |  | 2.59 |  | (from Fig 17-17) | ftpr |  | 2.59 |  | (from Fig 17-17)
ΔPf | = | (0.0224*2.59*1.939*(22.07)2*0.75)/(0.14623*6)=46.7 | psi | (from Eq.17-42) | ΔPf | = | 46.7493 | psi | (from Eq.17-42)
HLf |  | 0.13 |  | (from Fig 17-19) | HLf |  | 0.13 |  | (from Fig 17-19)
ΔPe | = | [(55*0.13)/144]*100=4.97 | psi | (from Eq.17-50) | ΔPe | = | 4.9653 | psi | (from Eq.17-50)
ΔPt | = | 46.75 + 4.97=51.71 | psi | (from Eq.17-52) | ΔPt | = | 51.7146 | psi | (from Eq.17-52)
Exit pressure P2 | = | 400-51.71=348 | psia |  | Exit pressure P2 | = | 348.2854 | psia
NLv | = | 1.938*0.849*(55/15)0.25=2.28 |  | (from Eq.17-54) | NLv | = | 2.2764 |  | (from Eq.17-54)
Ngv | = | 1.938*21.22*(55/15)0.25=56.91 |  | (from Eq.17-55) | Ngv | = | 56.9089 |  | (from Eq.17-55)
Nd | = | 10.073*6*(55/15)0.5=116 |  | (from Eq.17-56) | Nd | = | 115.73 |  | (from Eq.17-56)
NL | = | 0.15726*20*(1/(55*153))0.25=0.152 |  | (from Eq.17-57) | NL | = | 0.15153 |  | (from Eq.17-57)
NE | = | [1.84*(2.276)0.575*(400/14.73)0.05*(0.152)0.1]/[56.91*(115.73)0.0277]=0.044 |  | (from Eq.17-53) | NE | = | 0.044426 |  | (from Eq.17-53)
HLe |  | 0.14 |  | (from Fig 17-20) | HLe |  | 0.14 |  | (from Fig 17-20)
Liquid inventory IL | = | 28.80*0.14*62*0.75=109 | ft3 | (from Eq.17-58) | Liquid inventory IL | = | 108.864 | ft3 | (from Eq.17-58)
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processors Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.

## Limits
GPSA Engineering Data Book 14th Edition
LIMITS
For short runs of pipe where pressure drop is less than 10% of total pressure, such as within plant or battery limits, use the simplified Darcy formula, Eq. 17-31.
C2 factor (Fig. 17-9) is based on clean steel pipe. Internal pipe roughness in old or used pipe can significantly increase pressure drop.
Calculations of pressure drop due to multiple elevation changes in hilly terrain should use the sum of the uphill pipe runs. Pressure recovery in downhill sections is mostly ignored by the various correlations.
The sample calculations, equations and spreadsheets presented herein were developed using examples published in the Engineering Data Book as published by the Gas Processors Suppliers Association as a service to the gas processing industry. All information and calculation formulae has been compiled and edited in cooperation with Gas Processors Association (GPA).
While every effort has been made to present accurate and reliable technical information and calculation spreadsheets based on the GPSA Engineering Data Book sample calculations, the use of such information is voluntary and the GPA and GPSA do not guarantee the accuracy, completeness, efficacy, or timeliness of such information. Reference herein to any specific commercial product, calculation method, process, or service by trade-name, trademark, and service mark manufacturer or otherwise does not constitute or imply endorsement, recommendation or favoring by the GPA and/or GPSA.
The Calculation Spreadsheets are provided without warranty of any kind including warranties of accuracy or reasonableness of factual or scientific assumptions, studies or conclusions, or merchantability, fitness for a particular purpose, or non-infringement of intellectual property.
In no event will the GPA or GPSA and their members be liable for any damages whatsoever (including without limitation, those resulting from lost profits, lost data or business interruption) arising from the use, inability to, reference to or reliance on the information in this Publication, whether based on warranty, contract, tort or any other legal theory and whether or not advised of the possibility of such damages.
These calculation spreadsheets are provided to provide an “Operational level” of accuracy calculation based on rather broad assumptions (including but not limited to: temperatures, pressures, compositions, imperial curves, site conditions etc) and do not replace detailed and accurate Design Engineering taking into account actual process conditions, fluid properties, equipment condition or fowling and actual control set-point dead-band limitations.